## Inputs
Bank of America - Broomfield, CO (CO1-111) ¦ METAL FRAMING & DRYWALL TAKEOFF
Bid set: boa_SIN_MARKUPS.pdf · 2026-10-21 · Edit ONLY the yellow cells.
PARAMETER | VALUE | NOTE / SOURCE
Waste - ALL METAL, any type | 0.15 | Estimator standing rule: 15% on everything that is metal.
Waste - EVERYTHING THAT IS NOT METAL | 0.06 | Estimator standing rule: same figure as board.
Board sheet width (ft) | 4 | Sheet size is a parameter; buy the size that wastes least.
Board sheet length (ft) | 12 | Change it and every sheet count re-rounds.
SF per board sheet | 48 | Width x length.
Stud stock length (ft) | 20 | Stud, header, framed opening and stud blocking: sticks.
Track stock length (ft) | 10 | Track, sill track and purlin: runs.
Floor plan scale (pt/ft) | 18 | Project value (canon constants).
B.O. Deck (ft) | n/a | Project value (canon constants).
T.O. Parapet (ft) | n/a | Project value (canon constants).
Sealant coverage (LF per tube) | 25 | Sealant yield per tube - set your supplier's figure.
C.R. channel stock length (ft) | 16 | 1-1/2" cold-rolled channel (bracing, carrying channel).
Hat / furring channel stock (ft) | 12 | 7/8" hat furring channel.
Trim stick length (ft) | 10 | Corner bead, casing bead, shadow molding, PVC trim.
Hanger wire purchase | continuous coil (LF) | Bought by LF from a continuous coil; the hanger count goes on its own PCS row.
Drywall screws per SF of board | 1.2 | YIELD (GA-216 field / perimeter spacing).
Framing screws per stud piece | 4 | YIELD: 2 per stud-to-track connection, each end.
Power-driven pin spacing (ft) | 1 | YIELD: bottom track on slab, interior walls.
Joint compound (lb per SF) | 0.072 | YIELD: 72 lb per 1,000 SF, level 4 (estimator criterion).
Joint tape (LF per SF) | 0.37 | YIELD: 370 LF per 1,000 SF.
Expansion anchor spacing (ft) | 0.6667 | YIELD: exterior bottom track on slab.

## Partition Takeoff
ORGANIZED PARTITION TAKEOFF - Bank of America - Broomfield, CO (CO1-111)
Grouped by partition type. Every row cites its DETAIL/SHEET and its status.
Partition / Scope | Wall # | Length (LF) | Height (FT) | Layers | Stud Size | Stud O.C. (in) | Board (SF) | Location | Source (DETAIL/SHEET) | Status
TYPE EXT-6CFMF
EXT-6CFMF #A-EXT-N1 - North facade, grid F, Office 1 ME 105 (from the Central Zone storefront jamb to the NE corner) | A-EXT-N1 | 13.604 | 14.358 | 1 | 6" | 16 | 209.16 | North facade, grid F, Office 1 ME 105 (from the Central Zone storefront jamb to the NE corner) | 5/A09.26 | [DERIVED]
EXT-6CFMF #A-EXT-E1+A-EXT-E2 - East facade, grid 8, Offices 105-108 and Cash Window 116 (high zone, F to B) + East facade, grid 8, Cash Window 116 / Work Room 119 (low zone, B to A) | A-EXT-E1+A-EXT-E2 | 75.34 | 13.462 | 1 | 6" | 16 | 1025.91 | East facade, grid 8, Offices 105-108 and Cash Window 116 (high zone, F to B) + East facade, grid 8, Cash Window 116 / Work Room 119 (low zone, B to A) | 5/A09.26 | [DERIVED]
EXT-6CFMF #A-EXT-S1+A-EXT-S2 - South facade, grid A, grids 3 to 6 (Wellness 115, Corridor 111 / door 123, NER 121, Break Room 118) + South facade, grid A, grids 6 to 8 (Break Room 118, Work Room 119) | A-EXT-S1+A-EXT-S2 | 53.5 | 11.172 | 1 | 6" | 16 | 643.2 | South facade, grid A, grids 3 to 6 (Wellness 115, Corridor 111 / door 123, NER 121, Break Room 118) + South facade, grid A, grids 6 to 8 (Break Room 118, Work Room 119) | 5/A09.26 | [DERIVED]
EXT-6CFMF #A-EXT-W3A+A-EXT-W3B - West facade, grid 3, Offices 109 / 110 (high zone, D to B) + West facade, grid 3, restrooms 114 / 113, Janitor 112, Wellness 115 (low zone, B to A) | A-EXT-W3A+A-EXT-W3B | 46.947 | 12.919 | 1 | 6" | 16 | 623.36 | West facade, grid 3, Offices 109 / 110 (high zone, D to B) + West facade, grid 3, restrooms 114 / 113, Janitor 112, Wellness 115 (low zone, B to A) | 5/A09.26 | [DERIVED]
EXT-6CFMF #A-EXT-WJ - West drive-up recess: jog on line D between grid 2 and grid 3 (south face of ATM Room 102); faces south, kept in the W facade with the drive-up canopy (same as A-CEIL canopy band W) | A-EXT-WJ | 4.848 | 14.358 | 1 | 6" | 16 | 74.54 | West drive-up recess: jog on line D between grid 2 and grid 3 (south face of ATM Room 102); faces south, kept in the W facade with the drive-up canopy (same as A-CEIL canopy band W) | 5/A09.26 | [DERIVED]
EXT-6CFMF #A-EXT-W2 - West facade, grid 2, 24 HR Vestibule 101 and ATM Room 102 (drive-up ATM) | A-EXT-W2 | 20.9 | 14.358 | 1 | 6" | 16 | 315.57 | West facade, grid 2, 24 HR Vestibule 101 and ATM Room 102 (drive-up ATM) | 5/A09.26 | [DERIVED]
TYPE CANOPY-COL
CANOPY-COL #A-EXT-CW1 - Drive-up canopy column on grid 1 near grid G (west of the building) | A-EXT-CW1 | 5.667 | 10.604 | 0 | 3-5/8" | 16 | 0 | Drive-up canopy column on grid 1 near grid G (west of the building) | 5/A09.25 | [DERIVED]
CANOPY-COL #A-EXT-CW2 - Drive-up canopy column on grid 1 near grid E.4 (west of the building) | A-EXT-CW2 | 5.667 | 10.604 | 0 | 3-5/8" | 16 | 0 | Drive-up canopy column on grid 1 near grid E.4 (west of the building) | 5/A09.25 | [DERIVED]
CANOPY-COL #A-EXT-CW3 - Drive-up canopy column on grid 1 near grid C.5 (west of the building) | A-EXT-CW3 | 5.667 | 10.604 | 0 | 3-5/8" | 16 | 0 | Drive-up canopy column on grid 1 near grid C.5 (west of the building) | 5/A09.25 | [DERIVED]
CANOPY-COL #A-EXT-CW4 - Drive-up canopy column on grid 1 near grid B.2 (west of the building) | A-EXT-CW4 | 5.667 | 10.604 | 0 | 3-5/8" | 16 | 0 | Drive-up canopy column on grid 1 near grid B.2 (west of the building) | 5/A09.25 | [DERIVED]
TYPE EXT-PARAPET
EXT-PARAPET #A-PAR-G - North parapet line G, grids 2-4 (over the vestibule storefront and piers) | A-PAR-G | 16.2 | 4.292 | 0 | 6" parapet | 16 | 0 | North parapet line G, grids 2-4 (over the vestibule storefront and piers) | 4/A09.26 | [DERIVED]
EXT-PARAPET #A-PAR-4R - Return of the high parapet at grid 4 (south of line G, over the roof) | A-PAR-4R | 3.876 | 4.292 | 0 | 6" parapet | 16 | 0 | Return of the high parapet at grid 4 (south of line G, over the roof) | 4/A09.26 | [DERIVED]
EXT-PARAPET #A-PAR-F - North parapet line F, grids 4-8 | A-PAR-F | 40 | 2.042 | 0 | 6" parapet | 16 | 0 | North parapet line F, grids 4-8 | 4/A09.26 | [DERIVED]
EXT-PARAPET #A-PAR-8H+A-PAR-8L - East parapet grid 8, F to B (high roof) + East parapet grid 8, B to A (low roof) | A-PAR-8H+A-PAR-8L | 75.933 | 2.901 | 0 | 6" parapet | 16 | 0 | East parapet grid 8, F to B (high roof) + East parapet grid 8, B to A (low roof) | 4/A09.26 | [DERIVED]
EXT-PARAPET #A-PAR-A - South parapet line A, grids 3-8 | A-PAR-A | 52.333 | 4.885 | 0 | 6" parapet | 16 | 0 | South parapet line A, grids 3-8 | 4/A09.26 | [DERIVED]
EXT-PARAPET #A-PAR-3H+A-PAR-3L - West parapet grid 3, D to B + West parapet grid 3, B to A | A-PAR-3H+A-PAR-3L | 47.927 | 3.403 | 0 | 6" parapet | 16 | 0 | West parapet grid 3, D to B + West parapet grid 3, B to A | 4/A09.26 | [DERIVED]
EXT-PARAPET #A-PAR-D - Jog parapet line D, grids 2-3 (end of the high parapet) | A-PAR-D | 3.867 | 4.292 | 0 | 6" parapet | 16 | 0 | Jog parapet line D, grids 2-3 (end of the high parapet) | 4/A09.26 | [DERIVED]
EXT-PARAPET #A-PAR-2 - West parapet grid 2, G to D (high parapet) | A-PAR-2 | 29 | 4.292 | 0 | 6" parapet | 16 | 0 | West parapet grid 2, G to D (high parapet) | 4/A09.26 | [DERIVED]
TYPE F
F #A-INT-001 - Diagonal ATM partition between 24 HR Vestibule 101 (NE side) and ATM Room 102 (SW side) | A-INT-001 | 17.747 | 15.375 | 2 | 3-5/8" | 16 | 325.1 | Diagonal ATM partition between 24 HR Vestibule 101 (NE side) and ATM Room 102 (SW side) | 12/A12.01 | [DERIVED]
TYPE B2
B2 #A-INT-002 - ATM Room 102 east wall to Central Zone 103 (grid 4) | A-INT-002 | 5.667 | 15.375 | 2 | 6" | 16 | 111.64 | ATM Room 102 east wall to Central Zone 103 (grid 4) | 1/A12.01 | [CONFIRMED]
B2 #A-INT-030 - Break Room 118 / Work Room 119 wall | A-INT-030 | 11.407 | 11.631 | 2 | 6" | 16 | 265.34 | Break Room 118 / Work Room 119 wall | 1/A12.01 | [DERIVED]
B2 #A-INT-044a+A-INT-044b - Women's Restroom 114 east wall to Corridor 111, north of grid B (high deck zone) + Women's Restroom 114 east wall to Corridor 111 (door 114), south of grid B (low deck zone) | A-INT-044a+A-INT-044b | 5.542 | 13.239 | 2 | 6" | 16 | 98.96 | Women's Restroom 114 east wall to Corridor 111, north of grid B (high deck zone) + Women's Restroom 114 east wall to Corridor 111 (door 114), south of grid B (low deck zone) | 1/A12.01 | [DERIVED]
B2 #A-INT-045 - Men's 113 / Storage 117 / Wellness 115 east wall to Corridor 111 (doors 113, 117, 115) | A-INT-045 | 15.787 | 12.863 | 2 | 6" | 16 | 262.8 | Men's 113 / Storage 117 / Wellness 115 east wall to Corridor 111 (doors 113, 117, 115) | 1/A12.01 | [DERIVED]
TYPE G
G #A-INT-003 - ATM Room 102 / Office 5 CB 109 wall | A-INT-003 | 12.333 | 15.375 | 4 | 1-5/8" | 16 | 758.5 | ATM Room 102 / Office 5 CB 109 wall | 5/A12.01 | [DERIVED]
G #A-INT-005 - Office 5 CB 109 / Office 6 CB 110 wall | A-INT-005 | 11.625 | 15.375 | 4 | 1-5/8" | 16 | 714.94 | Office 5 CB 109 / Office 6 CB 110 wall | 5/A12.01 | [CONFIRMED]
G #A-INT-007 - Office 6 CB 110 / Women's Restroom 114 wall | A-INT-007 | 11.625 | 15.375 | 4 | 1-5/8" | 16 | 714.94 | Office 6 CB 110 / Women's Restroom 114 wall | 5/A12.01 | [CONFIRMED]
G #A-INT-028 - Office 4 CB 108 / Cash Window 116 wall | A-INT-028 | 10.073 | 15.375 | 4 | 1-5/8" | 16 | 619.51 | Office 4 CB 108 / Cash Window 116 wall | 5/A12.01 | [DERIVED]
G #A-INT-033 - Office 2 CL 106 / Office 3 SB 107 wall | A-INT-033 | 11.771 | 15.375 | 4 | 1-5/8" | 16 | 723.9 | Office 2 CL 106 / Office 3 SB 107 wall | 5/A12.01 | [CONFIRMED]
G #A-INT-034 - Office 3 SB 107 / Office 4 CB 108 wall | A-INT-034 | 11.771 | 15.375 | 4 | 1-5/8" | 16 | 723.9 | Office 3 SB 107 / Office 4 CB 108 wall | 5/A12.01 | [CONFIRMED]
G #A-INT-035 - Office front OF-E north stub (Central Zone / Office 1 ME 105) | A-INT-035 | 2.42 | 14.383 | 4 | 1-5/8" | 16 | 139.24 | Office front OF-E north stub (Central Zone / Office 1 ME 105) | 5/A12.01 | [DERIVED]
G #A-INT-036 - Office front OF-E stub at Office 105 / 106 | A-INT-036 | 3.467 | 14.383 | 4 | 1-5/8" | 16 | 199.45 | Office front OF-E stub at Office 105 / 106 | 5/A12.01 | [DERIVED]
G #A-INT-037 - Office front OF-E stub at Office 106 / 107 | A-INT-037 | 3.253 | 15.375 | 4 | 1-5/8" | 16 | 200.08 | Office front OF-E stub at Office 106 / 107 | 5/A12.01 | [DERIVED]
G #A-INT-038 - Office front OF-E stub at Office 107 / 108 | A-INT-038 | 3.253 | 14.225 | 4 | 1-5/8" | 16 | 185.11 | Office front OF-E stub at Office 107 / 108 | 5/A12.01 | [DERIVED]
TYPE G1
G1 #A-INT-004 - Office front OF-W stub between Office 5 CB 109 / Office 6 CB 110 and Central Zone | A-INT-004 | 3.507 | 15.375 | 4 | 1-5/8" | 16 | 215.66 | Office front OF-W stub between Office 5 CB 109 / Office 6 CB 110 and Central Zone | 5/A12.01 | [DERIVED]
G1 #A-INT-006 - Office front OF-W south stub (Office 6 CB 110 / Central Zone) | A-INT-006 | 3.18 | 15.375 | 4 | 1-5/8" | 16 | 195.58 | Office front OF-W south stub (Office 6 CB 110 / Central Zone) | 5/A12.01 | [DERIVED]
G1 #A-INT-032 - Office 1 ME 105 / Office 2 CL 106 wall | A-INT-032 | 11.771 | 15.375 | 4 | 1-5/8" | 16 | 723.9 | Office 1 ME 105 / Office 2 CL 106 wall | 5/A12.01 | [CONFIRMED]
TYPE A1
A1 #A-INT-008 - Corridor 111 north wall to Central Zone (door 111) | A-INT-008 | 5.583 | 15.375 | 2 | 3-5/8" | 16 | 62.81 | Corridor 111 north wall to Central Zone (door 111) | 3/A12.01 | [CONFIRMED]
A1 #A-INT-010 - MW01 cabinet recess east wall (Calling Cubes 122) | A-INT-010 | 3.533 | 15.375 | 2 | 3-5/8" | 16 | 63.6 | MW01 cabinet recess east wall (Calling Cubes 122) | 3/A12.01 | [DERIVED]
A1 #A-INT-011 - MW01 cabinet recess south wall (Calling Cubes 122) | A-INT-011 | 2.02 | 15.375 | 2 | 3-5/8" | 16 | 36.36 | MW01 cabinet recess south wall (Calling Cubes 122) | 3/A12.01 | [DERIVED]
A1 #A-INT-012 - Calling Cubes 122 north wall to Waiting 104 | A-INT-012 | 17.02 | 15.375 | 2 | 3-5/8" | 16 | 348.91 | Calling Cubes 122 north wall to Waiting 104 | 3/A12.01 | [DERIVED]
A1 #A-INT-015 - Calling Cubes 122 south wall to Break Room 118 | A-INT-015 | 15.812 | 12.969 | 2 | 3-5/8" | 16 | 284.62 | Calling Cubes 122 south wall to Break Room 118 | 3/A12.01 | [CONFIRMED]
A1 #A-INT-017 - Corridor 111 east wall to Break Room 118 / Electrical 120 / NER 121 (door 118B) | A-INT-017 | 20.52 | 11.819 | 2 | 3-5/8" | 16 | 360.89 | Corridor 111 east wall to Break Room 118 / Electrical 120 / NER 121 (door 118B) | 3/A12.01 | [DERIVED]
A1 #A-INT-021 - Break Room 118 NE return below Calling Cubes SE corner | A-INT-021 | 1.733 | 11.819 | 2 | 3-5/8" | 16 | 32.07 | Break Room 118 NE return below Calling Cubes SE corner | 3/A12.01 | [DERIVED]
A1 #A-INT-022 - Break Room 118 north wall to Cash Window customer area (door 118A) | A-INT-022 | 5.5 | 12.925 | 2 | 3-5/8" | 16 | 47.31 | Break Room 118 north wall to Cash Window customer area (door 118A) | 3/A12.01 | [CONFIRMED]
A1 #A-INT-031 - Work Room 119 north wall to Cash Window 116 (door 119) | A-INT-031 | 11.667 | 12.773 | 2 | 3-5/8" | 16 | 168.05 | Work Room 119 north wall to Cash Window 116 (door 119) | 3/A12.01 | [CONFIRMED]
TYPE A5
A5 #A-INT-009 - Calling Cubes 122 west wall (MW01 recessed cabinet + FEC-1) | A-INT-009 | 14.127 | 15.375 | 2 | 6" | 16 | 244.58 | Calling Cubes 122 west wall (MW01 recessed cabinet + FEC-1) | 3/A12.01 | [DERIVED]
A5 #A-INT-014a+A-INT-014b - Calling Cubes 122 east wall, north of grid B (high) + Calling Cubes 122 east wall, south of grid B (low) | A-INT-014a+A-INT-014b | 19.407 | 14.227 | 2 | 6" | 16 | 378.92 | Calling Cubes 122 east wall, north of grid B (high) + Calling Cubes 122 east wall, south of grid B (low) | 3/A12.01 | [DERIVED]
A5 #A-INT-016a+A-INT-016b - Corridor 111 east wall to Calling Cubes 122, north of grid B (high) + Corridor 111 east wall to Calling Cubes 122, south of grid B (door 122) | A-INT-016a+A-INT-016b | 4.873 | 14.433 | 2 | 6" | 16 | 39.94 | Corridor 111 east wall to Calling Cubes 122, north of grid B (high) + Corridor 111 east wall to Calling Cubes 122, south of grid B (door 122) | 3/A12.01 | [DERIVED]
A5 #A-INT-029 - Cash Window 116 west wall to Break Room 118 (door 116) | A-INT-029 | 6.938 | 11.774 | 2 | 6" | 16 | 80.57 | Cash Window 116 west wall to Break Room 118 (door 116) | 3/A12.01 | [CONFIRMED]
TYPE C1
C1 #A-INT-013+A-INT-013RW+A-INT-013RE - Furred monitor box on the north face of Calling Cubes north wall (keynote 7, 85" display) + West 8" return of the C1 furred monitor box, north face of Calling Cubes (keynote 7) + East 8" return of the C1 furred monitor box, north face of Calling Cubes (keynote 7) | A-INT-013+A-INT-013RW+A-INT-013RE | 11.333 | 15.375 | 1 | 3-5/8" | 16 | 174.25 | Furred monitor box on the north face of Calling Cubes north wall (keynote 7, 85" display) + West 8" return of the C1 furred monitor box, north face of Calling Cubes (keynote 7) + East 8" return of the C1 furred monitor box, north face of Calling Cubes (keynote 7) | 6/A12.01 | [DERIVED]
C1 #A-INT-025 - Furring at Future FCAM south of the teller line (Cash Window 116) | A-INT-025 | 2.98 | 12.923 | 1 | 3-5/8" | 16 | 38.51 | Furring at Future FCAM south of the teller line (Cash Window 116) | 6/A12.01 | [DERIVED]
C1 #A-INT-039 - Restroom plumbing chase, Women's Restroom 114 face | A-INT-039 | 10.027 | 12.924 | 1 | 3-5/8" | 16 | 129.58 | Restroom plumbing chase, Women's Restroom 114 face | 6/A12.01 | [DERIVED]
C1 #A-INT-040 - Restroom plumbing chase, Men's Restroom 113 face | A-INT-040 | 10.027 | 12.894 | 1 | 3-5/8" | 16 | 129.29 | Restroom plumbing chase, Men's Restroom 113 face | 6/A12.01 | [DERIVED]
C1 #A-INT-049 - Interior column box at the VEST-S / VEST-E corner (grille 103 north jamb, grid 4) | A-INT-049 | 4 | 15.375 | 1 | 3-5/8" | 16 | 61.52 | Interior column box at the VEST-S / VEST-E corner (grille 103 north jamb, grid 4) | 3/A08.21 | [DERIVED]
C1 #A-INT-050 - Interior column box at grille 103 south jamb / 24 HR Vestibule SE corner (grid 4 / E) | A-INT-050 | 2.533 | 15.375 | 1 | 3-5/8" | 16 | 38.95 | Interior column box at grille 103 south jamb / 24 HR Vestibule SE corner (grid 4 / E) | 3/A08.21 | [DERIVED]
C1 #A-INT-051 - NE storefront pier (grid 4 / G), interior C1 faces (Vestibule 100 / Central Zone 103) | A-INT-051 | 4.051 | 15.375 | 1 | 3-5/8" | 16 | 62.29 | NE storefront pier (grid 4 / G), interior C1 faces (Vestibule 100 / Central Zone 103) | 2/A09.25 | [DERIVED]
C1 #A-INT-052 - NW storefront pier (grid 2 / G), interior C1 faces (Vestibule 100) | A-INT-052 | 3.132 | 15.375 | 1 | 3-5/8" | 16 | 48.15 | NW storefront pier (grid 2 / G), interior C1 faces (Vestibule 100) | 1/A09.25 | [DERIVED]
TYPE B
B #A-INT-018 - Electrical 120 north wall to Break Room 118 | A-INT-018 | 9.987 | 12.829 | 2 | 3-5/8" | 16 | 256.24 | Electrical 120 north wall to Break Room 118 | 1/A12.01 | [DERIVED]
B #A-INT-019 - Electrical 120 / NER 121 east wall to Break Room 118 (doors 120, 121) | A-INT-019 | 13.74 | 12.829 | 2 | 3-5/8" | 16 | 257 | Electrical 120 / NER 121 east wall to Break Room 118 (doors 120, 121) | 1/A12.01 | [DERIVED]
B #A-INT-020 - Electrical 120 / NER 121 wall | A-INT-020 | 9.583 | 12.701 | 2 | 3-5/8" | 16 | 243.42 | Electrical 120 / NER 121 wall | 1/A12.01 | [CONFIRMED]
B #A-INT-046 - Men's Restroom 113 south wall to Janitor 112 / Storage 117 (door 112) | A-INT-046 | 11.729 | 12.75 | 2 | 3-5/8" | 16 | 251.35 | Men's Restroom 113 south wall to Janitor 112 / Storage 117 (door 112) | 1/A12.01 | [CONFIRMED]
B #A-INT-047 - Janitor Closet 112 / Storage 117 wall | A-INT-047 | 3.5 | 12.741 | 2 | 3-5/8" | 16 | 89.18 | Janitor Closet 112 / Storage 117 wall | 1/A12.01 | [CONFIRMED]
B #A-INT-048 - Janitor 112 / Storage 117 south wall to Wellness 115 | A-INT-048 | 11.729 | 12.669 | 2 | 3-5/8" | 16 | 297.25 | Janitor 112 / Storage 117 south wall to Wellness 115 | 1/A12.01 | [CONFIRMED]
TYPE A1K
A1K #A-INT-023 - Teller line south ballistic wall, west segment (Cash Window 116) | A-INT-023 | 1.767 | 12.925 | 2 | 3-5/8" | 24 | 45.66 | Teller line south ballistic wall, west segment (Cash Window 116) | 4/A12.01 | [DERIVED]
A1K #A-INT-024 - Teller line south ballistic wall, east segment (Cash Window 116 / Future FCAM) | A-INT-024 | 3.417 | 12.937 | 2 | 3-5/8" | 24 | 88.4 | Teller line south ballistic wall, east segment (Cash Window 116 / Future FCAM) | 4/A12.01 | [CONFIRMED]
A1K #A-INT-027 - Teller line north ballistic wall, east segment (Cash Window 116) | A-INT-027 | 3.417 | 15.375 | 2 | 3-5/8" | 24 | 105.06 | Teller line north ballistic wall, east segment (Cash Window 116) | 4/A12.01 | [CONFIRMED]
TYPE B2K
B2K #A-INT-026 - Teller line north ballistic wall, west segment (Office 4 CB 108 / Cash Window 116) | A-INT-026 | 1.773 | 15.375 | 2 | 6" | 24 | 54.52 | Teller line north ballistic wall, west segment (Office 4 CB 108 / Cash Window 116) | 4/A12.01 | [DERIVED]
TYPE BULKHEAD-G
BULKHEAD-G #A-INT-056+A-INT-057+A-INT-058+A-INT-059 - Central Zone 103 / Waiting 104 (ACT-4 field) / Office 1 ME 105 / underside of the CONT. BOX BEAM (bulkhead soffit over the opening) + Central Zone 103 / Waiting 104 (ACT-4 field) / Office 2 CL 106 / underside of the CONT. BOX BEAM (bulkhead soffit over the opening) + Central Zone 103 / Waiting 104 (ACT-4 field) / Office 3 SB 107 / underside of the CONT. BOX BEAM (bulkhead soffit over the opening) + Central Zone 103 / Waiting 104 (ACT-4 field) / Office 4 CB 108 / underside of the CONT. BOX BEAM (bulkhead soffit over the opening) | A-INT-056+A-INT-057+A-INT-058+A-INT-059 | 30 | 6.262 | 5 | 1-5/8" | 16 | 766.88 | Central Zone 103 / Waiting 104 (ACT-4 field) / Office 1 ME 105 / underside of the CONT. BOX BEAM (bulkhead soffit over the opening) + Central Zone 103 / Waiting 104 (ACT-4 field) / Office 2 CL 106 / underside of the CONT. BOX BEAM (bulkhead soffit over the opening) + Central Zone 103 / Waiting 104 (ACT-4 field) / Office 3 SB 107 / underside of the CONT. BOX BEAM (bulkhead soffit over the opening) + Central Zone 103 / Waiting 104 (ACT-4 field) / Office 4 CB 108 / underside of the CONT. BOX BEAM (bulkhead soffit over the opening) | 9/A12.01 | [DERIVED]
BULKHEAD-G #A-INT-060+A-INT-061 - Central Zone 103 / Waiting 104 (ACT-4 field) / Office 5 CB 109 / underside of the CONT. BOX BEAM (bulkhead soffit over the opening) + Central Zone 103 / Waiting 104 (ACT-4 field) / Office 6 CB 110 / underside of the CONT. BOX BEAM (bulkhead soffit over the opening) | A-INT-060+A-INT-061 | 15 | 7.375 | 5 | 1-5/8" | 16 | 453.08 | Central Zone 103 / Waiting 104 (ACT-4 field) / Office 5 CB 109 / underside of the CONT. BOX BEAM (bulkhead soffit over the opening) + Central Zone 103 / Waiting 104 (ACT-4 field) / Office 6 CB 110 / underside of the CONT. BOX BEAM (bulkhead soffit over the opening) | 9/A12.01 | [DERIVED]
| TOTAL - PARTITIONS | 955.6 |  |  |  |  | 15809.5
TYPE OTHER FRAMING (NOT A PARTITION)
fascia_box #A-FAS-N - N fascia, outer corner to outer corner (owns NW & NE corners) | A-FAS-N | 78.161 | 1.865 | 0 | 3-5/8" | 16 | 0 | N fascia, outer corner to outer corner (owns NW & NE corners) | 3/A09.26 | [DERIVED]
fascia_box #A-FAS-W - W (drive-up) fascia, from N fascia inner face to S return outer face | A-FAS-W | 55.994 | 1.865 | 0 | 3-5/8" | 16 | 0 | W (drive-up) fascia, from N fascia inner face to S return outer face | 16/A09.27 | [DERIVED]
fascia_box #A-FAS-WS - drive-up canopy south return at grid B (W canopy, separate line) | A-FAS-WS | 20.983 | 1.865 | 0 | 3-5/8" | 16 | 0 | drive-up canopy south return at grid B (W canopy, separate line) | 16/A09.27 | [DERIVED]
fascia_box #A-FAS-E - E fascia, from N fascia inner face to S return outer face | A-FAS-E | 52.056 | 1.865 | 0 | 3-5/8" | 16 | 0 | E fascia, from N fascia inner face to S return outer face | 7/A09.26 | [DERIVED]
fascia_box #A-FAS-ES - E canopy south return (wall to fascia) | A-FAS-ES | 2.467 | 1.865 | 0 | 3-5/8" | 16 | 0 | E canopy south return (wall to fascia) | 7/A09.26 | [DERIVED]
fascia_box #A-FAS-S - S entrance canopy front fascia, outer corner to outer corner | A-FAS-S | 23 | 1.865 | 0 | 3-5/8" | 16 | 0 | S entrance canopy front fascia, outer corner to outer corner | 7/A09.26 | [DERIVED]
fascia_box #A-FAS-SW - S canopy west return (wall to front fascia) | A-FAS-SW | 2.467 | 1.865 | 0 | 3-5/8" | 16 | 0 | S canopy west return (wall to front fascia) | 7/A09.26 | [DERIVED]
fascia_box #A-FAS-SE - S canopy east return (wall to front fascia) | A-FAS-SE | 2.467 | 1.865 | 0 | 3-5/8" | 16 | 0 | S canopy east return (wall to front fascia) | 7/A09.26 | [DERIVED]
storefront_cripples #A-EXT-SC-N-VEST - North facade, line G, above the Vestibule 100 storefront (grids 2-4) | A-EXT-SC-N-VEST | 12.562 | 4.983 | 1 | 6" | 16 | 86.37 | North facade, line G, above the Vestibule 100 storefront (grids 2-4) | 5/A09.26 | [DERIVED]
storefront_cripples #A-EXT-SC-N-CZ - North facade, line F, above the Central Zone 103 storefront (grid 4 pier to office wall) | A-EXT-SC-N-CZ | 26.25 | 4.525 | 1 | 6" | 16 | 180.47 | North facade, line F, above the Central Zone 103 storefront (grid 4 pier to office wall) | 5/A09.26 | [DERIVED]
storefront_cripples #A-EXT-SC-W-VEST - West facade, grid 2, above the Vestibule 100 west storefront | A-EXT-SC-W-VEST | 6.5 | 4.983 | 1 | 6" | 16 | 44.69 | West facade, grid 2, above the Vestibule 100 west storefront | 5/A09.26 | [DERIVED]
pier_part #A-EXT-P2 - Storefront pier at grid 2 / G (NW corner of Vestibule 100) | A-EXT-P2 | 3.375 | 14.358 | 0 | 6" | 16 | 0 | Storefront pier at grid 2 / G (NW corner of Vestibule 100) | 1/A09.25 | [DERIVED]
pier_part #A-EXT-P4 - Storefront pier at grid 4 / G (NE corner of Vestibule 100, west jamb of the Central Zone storefront) | A-EXT-P4 | 2.896 | 14.358 | 0 | 6" | 16 | 0 | Storefront pier at grid 4 / G (NE corner of Vestibule 100, west jamb of the Central Zone storefront) | 2/A09.25 | [DERIVED]
roof_step #A-EXT-RS1 - Roof step along grid B, grids 3-8: upper exterior row (low-roof side, above the low deck) | A-EXT-RS1 | 52.333 | 3.226 | 0 | 3-5/8" | 16 | 0 | Roof step along grid B, grids 3-8: upper exterior row (low-roof side, above the low deck) | 4/A02.02 | [DERIVED]
roof_step #A-EXT-RS2 - Roof step along grid B, grids 3-8: interior row (high side, high T/STEEL down to the bottom of the box) | A-EXT-RS2 | 52.333 | 3.584 | 2 | 3-5/8" | 16 | 255.15 | Roof step along grid B, grids 3-8: interior row (high side, high T/STEEL down to the bottom of the box) | 4/A02.02-GYP | [DERIVED]
roof_step #A-EXT-RS3 - Roof step along grid B, grids 3-8: lower row (below the low deck, low-roof side) | A-EXT-RS3 | 52.333 | 1.141 | 1 | 3-5/8" | 16 | 59.72 | Roof step along grid B, grids 3-8: lower row (below the low deck, low-roof side) | 4/A02.02-GYP | [DERIVED]
vestibule_head #VEST-HEAD-S - VEST-HEAD-S | VEST-HEAD-S | 15.646 | 5.375 | 0 | 3-5/8" | 16 | 0 | VEST-HEAD-S | 7/A12.10 | [DERIVED]
vestibule_head #VEST-HEAD-E - Central Zone 103 (ACT-4 11'-6" field) | VEST-HEAD-E | 6.417 | 4.383 | 1 | 3-5/8" | 16 | 28.13 | Central Zone 103 (ACT-4 11'-6" field) | 5/A12.10 | [DERIVED]
grille_head #A-INT-055 - Central Zone 103 (ACT-4 11'-6" field) / grille head soffit (underside, 24 HR Vestibule / Central Zone) | A-INT-055 | 13.333 | 3.875 | 2 | 2-1/2" | 16 | 24.44 | Central Zone 103 (ACT-4 11'-6" field) / grille head soffit (underside, 24 HR Vestibule / Central Zone) | 4/A08.21 | [DERIVED]
ceiling_transition #A-CTR-104N - WAITING - N edge of GB ceiling against ACT-4 (11.5' ACT vs 11.0' GB) | A-CTR-104N | 17.028 | 4.375 | 3 | 3-5/8" | 16 | 32.64 | WAITING - N edge of GB ceiling against ACT-4 (11.5' ACT vs 11.0' GB) | 7/A09.33 | [DERIVED]
ceiling_transition #A-CTR-104W - WAITING - W edge of GB ceiling against ACT-4 (11.5' ACT vs 11.0' GB) | A-CTR-104W | 30 | 4.375 | 3 | 3-5/8" | 16 | 57.5 | WAITING - W edge of GB ceiling against ACT-4 (11.5' ACT vs 11.0' GB) | 7/A09.33 | [DERIVED]
ceiling_transition #A-CTR-104E - WAITING - E edge of GB ceiling against ACT-4 (11.5' ACT vs 11.0' GB) | A-CTR-104E | 30 | 4.375 | 3 | 3-5/8" | 16 | 57.5 | WAITING - E edge of GB ceiling against ACT-4 (11.5' ACT vs 11.0' GB) | 7/A09.33 | [DERIVED]
ceiling_transition #A-CTR-116NW - CASH WINDOW 116 - GB soffit strip north of grid B (high deck zone) - W edge of GB ceiling against ACT-4 (9.0' ACT vs 8.0' GB) | A-CTR-116NW | 6.439 | 7.375 | 3 | 3-5/8" | 16 | 15.56 | CASH WINDOW 116 - GB soffit strip north of grid B (high deck zone) - W edge of GB ceiling against ACT-4 (9.0' ACT vs 8.0' GB) | 7/A09.33 | [DERIVED]
ceiling_transition #A-CTR-116NE - CASH WINDOW 116 - GB soffit strip north of grid B (high deck zone) - E edge of GB ceiling against ACT-4 (9.0' ACT vs 8.0' GB) | A-CTR-116NE | 6.439 | 7.375 | 3 | 3-5/8" | 16 | 15.56 | CASH WINDOW 116 - GB soffit strip north of grid B (high deck zone) - E edge of GB ceiling against ACT-4 (9.0' ACT vs 8.0' GB) | 7/A09.33 | [DERIVED]
ceiling_transition #A-CTR-116SW - CASH WINDOW 116 - GB soffit strip south of grid B (LOW deck zone) - W edge of GB ceiling against ACT-4 (9.0' ACT vs 8.0' GB) | A-CTR-116SW | 5.572 | 5.052 | 3 | 3-5/8" | 16 | 13.47 | CASH WINDOW 116 - GB soffit strip south of grid B (LOW deck zone) - W edge of GB ceiling against ACT-4 (9.0' ACT vs 8.0' GB) | 7/A09.33 | [DERIVED]
ceiling_transition #A-CTR-116SE - CASH WINDOW 116 - GB soffit strip south of grid B (LOW deck zone) - E edge of GB ceiling against ACT-4 (9.0' ACT vs 8.0' GB) | A-CTR-116SE | 5.572 | 5.052 | 3 | 3-5/8" | 16 | 13.47 | CASH WINDOW 116 - GB soffit strip south of grid B (LOW deck zone) - E edge of GB ceiling against ACT-4 (9.0' ACT vs 8.0' GB) | 7/A09.33 | [DERIVED]
alcove #A-INT-041+A-INT-042+A-INT-043 - Lavatory niche north return (corridor niche between restrooms) + Lavatory niche back wall (lavatories, corridor niche) + Lavatory niche south return | A-INT-041+A-INT-042+A-INT-043 | 7.487 | 12.309 | 2 | 3-5/8" | 16 | 138.78 | Lavatory niche north return (corridor niche between restrooms) + Lavatory niche back wall (lavatories, corridor niche) + Lavatory niche south return | 3/A12.01 | [DERIVED]

## Material Summary
MATERIAL SUMMARY - NET / WASTE / PURCHASE
Waste lives HERE, in its own column, applied ONCE: Pieces = ROUNDUP(Net x (1 + waste) / stock). Every stock length, coverage and yield is an Inputs cell.
Material | Unit | Net | Waste % | Waste | Purchase | Selling unit | Pieces to buy | Where it comes from | Yield check (live formula)
6" metal stud (LF of material) | LF | 4656.26 | 0.15 | 698.439 | 5354.699 | stick 20 ft | 268 | familias_out.json '6" stud (all gauges)'; 1/A09.25; 2/A09.25; studs_out.json; cut_ft = piece length carrying the most LF in studs_out.json
3-5/8" metal stud (LF of material) | LF | 6994.55 | 0.15 | 1049.1825 | 8043.7325 | stick 20 ft | 403 | familias_out.json '3-5/8" stud (all gauges)'; 5/A09.25; studs_out.json; cut_ft = piece length carrying the most LF in studs_out.json
1-5/8" metal stud (LF of material) | LF | 3847.86 | 0.15 | 577.179 | 4425.039 | stick 20 ft | 222 | familias_out.json '1-5/8" stud'; 5/A12.01; studs_out.json; cut_ft = piece length carrying the most LF in studs_out.json
6" parapet infill stud (LF of material) | LF | 1001.46 | 0.15 | 150.219 | 1151.679 | stick 20 ft | 58 | familias_out.json '6" parapet stud'; 1/A09.01; 2/A09.01; 1/A09.02; 4/A09.26; cut_ft = piece length carrying the most LF in studs_out.json
Track, ceilings / soffits / canopy | LF | 1244.13 | 0.15 | 186.6195 | 1430.7495 | run 10 ft | 144 | familias_out.json 'ceiling / soffit track'; corridas_out.json
Bracing 1-1/2" C.R. channel | LF | 2509.27 | 0.15 | 376.3905 | 2885.6605 | C.R. channel 16 ft | 181 | familias_out.json 'bracing C.R. channel'; corridas_out.json
Purlin, top track to deck | LF | 313.57 | 0.15 | 47.0355 | 360.6055 | run 10 ft | 37 | familias_out.json 'purlin (track to deck)'; corridas_out.json
Header / metal stud box beam | LF | 796.79 | 0.15 | 119.5185 | 916.3085 | stick 20 ft | 46 | familias_out.json 'header / box beam'; headers_in.json; 7/S5.20
Sill track | LF | 119.12 | 0.15 | 17.868 | 136.988 | run 10 ft | 14 | familias_out.json 'sill track'; headers_in.json; 7/S5.20
Furring channel (ceilings) | LF | 815.83 | 0.15 | 122.3745 | 938.2045 | hat channel 12 ft | 79 | familias_out.json 'furring channel'; A04.01
Carrying channel (ceilings) | LF | 336.03 | 0.15 | 50.4045 | 386.4345 | C.R. channel 16 ft | 25 | familias_out.json 'carrying channel'; A04.01
Hanger wire | LF | 592.63 | 0.15 | 88.8945 | 681.5245 | continuous coil (LF) | 682 | familias_out.json 'hanger wire'; A04.01
Hanger wire 12 ga - hanger count (one per hanger, height per room) | PCS | 121 | 0 | 0 | 121 | each | 121 | familias_out.json hanger_pcs.total_pcs; wire bought on the LF row
Framed openings - MEP, light slots and diffusers | LF | 918.88 | 0.15 | 137.832 | 1056.712 | stick 20 ft | 53 | framed_openings_out.json 'framed openings MEP'; 6/A09.33; 4/A09.33
5/8" gypsum board, regular | SF | 17548.27 | 0.06 | 1052.8962 | 18601.1662 | 4x12 sheet | 388 | familias_out.json '5/8" gyp board regular (walls + ceilings)'; board_out.json
5/8" gypsum board, MOISTURE RESISTANT | SF | 258.87 | 0.06 | 15.5322 | 274.4022 | 4x12 sheet | 6 | familias_out.json '5/8" gyp MOISTURE RESISTANT'; board_out.json
Ballistic panel UL752 | SF | 85.34 | 0.06 | 5.1204 | 90.4604 | 4x8 sheet | 3 | familias_out.json 'ballistic panel'; board_out.json
3/8" gypsum board | SF | 65.65 | 0.06 | 3.939 | 69.589 | 4x8 sheet | 3 | familias_out.json '3/8" gyp board'; board_out.json
5/8" glass mat sheathing (exterior face of the stud) | SF | 362.16 | 0.06 | 21.7296 | 383.8896 | 4x8 sheet | 12 | familias_out.json '5/8" glass mat sheathing'
5/8" EXTERIOR gypsum sheathing | SF | 952.24 | 0.06 | 57.1344 | 1009.3744 | 4x8 sheet | 32 | familias_out.json '5/8" EXTERIOR gyp sheathing'; board_out.json
FRP panels | SF | 334.75 | 0.06 | 20.085 | 354.835 | 4x8 sheet | 12 | familias_out.json 'FRP'; D/A08.01; 5/A08.01; 1/A08.01
Cement board (substrate under the FRP cove base band) | SF | 31.88 | 0.06 | 1.9128 | 33.7928 | 3x5 sheet | 3 | familias_out.json 'cement board'; 1/A08.01; 3/A08.01
Blocking FRT / 2X FRT wood | LF | 985.85 | 0.06 | 59.151 | 1045.001 | LF (lumber cut to length) | 1046 | familias_out.json 'FRT blocking'; 13/A12.02; 9/A12.02; 8/A12.01; 9/A12.01; 7/A11.01; 10/A12.01
Stud blocking at edge of gypboard (structural detail) | LF | 560.96 | 0.15 | 84.144 | 645.104 | stick 20 ft | 33 | familias_out.json metal_blocking_by_origin 'metal stud blocking (362CR / STUD BLOCKING)' (edge); 4/S5.20
Metal stud blocking at wall-mounted items (notes) | LF | 42.98 | 0.15 | 6.447 | 49.427 | stick 20 ft | 3 | familias_out.json metal_blocking_by_origin 'metal stud blocking (362CR / STUD BLOCKING)' (items); 4/S5.20
METAL trim - corner bead, casing bead, shadow molding, gypsum edge trim | LF | 1052.1 | 0.15 | 157.815 | 1209.915 | trim stick 10 ft | 121 | familias_out.json 'metal trim (corner bead, casing, shadow molding)'; 8/A12.01; 9/A12.01; 7/A11.01; 10/A12.01; 4/A08.21; 1/A08.21
Sealant at base of gypsum (exterior, not acoustical) | LF | 211.81 | 0.06 | 12.7086 | 224.5186 | tube (25 LF per tube) | 9 | familias_out.json sealant_exterior_lf 'sealant at base of gypsum (exterior)'; 5/A09.26; 9/A09.27 (not acoustical)
Bottom track 6" | LF | 300.67 | 0.15 | 45.1005 | 345.7705 | run 10 ft | 35 | familias_out.json track_by_element 'bottom track (all)' (R73.3)
Bottom track - other framing (not a partition type, see source) | LF | 64.92 | 0.15 | 9.738 | 74.658 | run 10 ft | 8 | familias_out.json track_by_element 'bottom track (all)' (R73.3)
Bottom track 3-5/8" | LF | 248.27 | 0.15 | 37.2405 | 285.5105 | run 10 ft | 29 | familias_out.json track_by_element 'bottom track (all)' (R73.3)
Parapet bottom track | LF | 269.15 | 0.15 | 40.3725 | 309.5225 | run 10 ft | 31 | familias_out.json track_by_element 'bottom track (all)' (R73.3)
Bottom track - roof step and heads (vestibule / bulkhead) | LF | 179.06 | 0.15 | 26.859 | 205.919 | run 10 ft | 21 | familias_out.json track_by_element 'bottom track (all)' (R73.3)
Bottom track 1-5/8" | LF | 290.1 | 0.15 | 43.515 | 333.615 | run 10 ft | 34 | familias_out.json track_by_element 'bottom track (all)' (R73.3)
Top / deflection track 6" | LF | 300.67 | 0.15 | 45.1005 | 345.7705 | run 10 ft | 35 | familias_out.json track_by_element 'top / deflection track (all)' (R73.3)
Top / deflection track - other framing (not a partition type, see source) | LF | 64.92 | 0.15 | 9.738 | 74.658 | run 10 ft | 8 | familias_out.json track_by_element 'top / deflection track (all)' (R73.3)
Top / deflection track 3-5/8" | LF | 248.27 | 0.15 | 37.2405 | 285.5105 | run 10 ft | 29 | familias_out.json track_by_element 'top / deflection track (all)' (R73.3)
Parapet top track | LF | 269.15 | 0.15 | 40.3725 | 309.5225 | run 10 ft | 31 | familias_out.json track_by_element 'top / deflection track (all)' (R73.3)
Top track - roof step and heads (vestibule / bulkhead) | LF | 179.06 | 0.15 | 26.859 | 205.919 | run 10 ft | 21 | familias_out.json track_by_element 'top / deflection track (all)' (R73.3)
Top / deflection track 1-5/8" | LF | 290.1 | 0.15 | 43.515 | 333.615 | run 10 ft | 34 | familias_out.json track_by_element 'top / deflection track (all)' (R73.3)
Blocking 2X wood (not labeled FRT) | LF | 4 | 0.06 | 0.24 | 4.24 | LF (lumber cut to length) | 5 | familias_out.json wood_blocking_lf 'FRT blocking' (v76)
5/8" FRT plywood sheathing (canopy and soffits) | SF | 1943.4 | 0.06 | 116.604 | 2060.004 | 4x12 ft sheet (Inputs) | 43 | familias_out.json FRT plywood by material; 1/A09.25; 2/A09.25; 12/A12.01; 3/A09.26; 16/A09.27; 7/A09.26; 5/A09.25; 11/A09.27
Exterior sheathing 5/8" FRT plywood bonded to 2-1/2" polyiso | SF | 3832.11 | 0.06 | 229.9266 | 4062.0366 | 4x12 ft sheet (Inputs) | 85 | familias_out.json FRT plywood by material; 1/A09.25; 2/A09.25; 12/A12.01; 3/A09.26; 16/A09.27; 7/A09.26; 5/A09.25; 11/A09.27
FRT plywood substrate (3/4 in.) | SF | 665.55 | 0.06 | 39.933 | 705.483 | 4x12 ft sheet (Inputs) | 15 | familias_out.json FRT plywood by material; 1/A09.25; 2/A09.25; 12/A12.01; 3/A09.26; 16/A09.27; 7/A09.26; 5/A09.25; 11/A09.27
3/4" FRT plywood at storefront piers | SF | 23.59 | 0.06 | 1.4154 | 25.0054 | 4x12 ft sheet (Inputs) | 1 | familias_out.json FRT plywood by material; 1/A09.25; 2/A09.25; 12/A12.01; 3/A09.26; 16/A09.27; 7/A09.26; 5/A09.25; 11/A09.27
5/8" FRT plywood at canopy column wraps | SF | 240.37 | 0.06 | 14.4222 | 254.7922 | 4x12 ft sheet (Inputs) | 6 | familias_out.json FRT plywood by material; 1/A09.25; 2/A09.25; 12/A12.01; 3/A09.26; 16/A09.27; 7/A09.26; 5/A09.25; 11/A09.27
Additional head track at openings over 4'-0" wide | LF | 56 | 0.15 | 8.4 | 64.4 | run 10 ft | 7 | accesorios.py [CRITERION]: 2/S5.20 HEAD TRACK @ NON LOAD BRG 'ADD FULL LENGTH ADDL HEAD TRACK @ OPNG >4'-0"'; Estimator user decision #1: R.O. + 1'-4" (8" bearing each side)
Stud reinforcement at MEP penetrations | PCS | 27 | 0 | 0 | 27 | each | 27 | accesorios.py [CRITERION]: 6/S5.20 (PENETRATION THRU STUDS: 16 GAUGE PLATE REINFORCEMENT REQD AT PENETRATIONS; 1" DIA. AND SMALLER OPENING CENTERED IN WEB; FLANGES SHALL NOT BE NOTCHED OR CUT); M01.01 (mep.cruces, registered to A02.01); 6/S5.20 plate; 6/S5.20 (PENETR
Extra framing - ATM recess (only what a detail prints at the recess; the wall stays in its type) | LF | 30 | 0.15 | 4.5 | 34.5 | stick 20 ft | 2 | accesorios.py [DERIVED]: 6/A08.11; 5/A08.11; 7/A08.11; A02.01 (p24) vector + A02.01 printed 30'-4 1/4" (grid 2, NW pier north face to jog outer face) minus printed 1'-11 3/4" (pier) and 6'-6" (storefront) minus the jog thickness (vector); 6/A08.11: "2 1/2" METAL ST
2-1/2" CFMF @ 16" O.C. at coiling grille head (4/A08.21) | LF | 31.05 | 0.15 | 4.6575 | 35.7075 | stick 20 ft | 2 | accesorios.py [DERIVED]: 4/A08.21 printed 1'-6" + 2'-4 1/2" (chain), '6" CFMF BOX BEAM HEADER' x 2, '5/8" GYP. BD., TYP.'
Gypsum board jamb return at openings | SF | 67.91 | 0.06 | 4.0746 | 71.9846 | 4x12 ft sheet (Inputs) | 2 | accesorios.py [CRITERION]: Estimator criterion (return width = 6" stud depth, not dimensioned; RFI with delta at 0.20 ft)
PVC trim - edge trim molding and inside corner molding at the FRP | LF | 223.5 | 0.06 | 13.41 | 236.91 | trim stick 10 ft | 24 | accesorios.py [DERIVED]: A,B,C,D/A08.01 '5'-0" TO TOP OF FRP' (WC-3 FRP panel, toilet room finish schedule); 1/A08.01 rectilinear L polygon (one step at the lavatory alcove); A05.01 finish key note 6 'FRP FROM FLOOR TO 4'-0" AFF, WIDTH TO MATCH WIDTH OF MOP SINK AT
Power-driven fasteners and duct sleeves | PCS | 298 | 0 | 0 | 298 | each | 298 | accesorios.py [DERIVED]: S5.10 parapet wall infill framing note 'PAFs SPACED AT 12" O.C. MAX.'; M01.01 (FD tags; position = tag xy + registration); M01.01 (mep.cruces, registered to A02.01); 6/S5.20 plate; M01.01 overlay ov_M0101_NE.png; opening_schedule
Access panel 2'x2' | PCS | 1 | 0 | 0 | 1 | each | 1 | accesorios.py [CONFIRMED]: A04.01 RCP key note 4 '2' X 2' LOCKING ACCESS PANEL. KEYED TO MATCH MAIN ENTRY.' (1 circle, Vestibule 100 GB 10'-0")
Drywall screws 1-1/4" bugle head | PCS | 21447.35 | 0 | 0 | 21447.35 | each | 21448 | accesorios.py [DERIVED]: Inputs!B20 (Drywall screws per SF of board = 1.2) x 17872.8 SF of board | 21447.36
Framing screws, pan head self-drilling | PCS | 7116 | 0 | 0 | 7116 | each | 7116 | accesorios.py [DERIVED]: Inputs!B21 (Framing screws per stud piece = 4) x 1779 stud pieces | 7116
Power-driven fasteners, slab pins for the bottom track | PCS | 533.86 | 0 | 0 | 533.86 | each | 534 | accesorios.py [DERIVED]: 533.86 LF of interior bottom track on slab / Inputs!B22 (Power-driven pin spacing (ft) = 1) | 533.86
Expansion anchors Hilti 1/4" Kwik Bolt II, exterior bottom track @ 8" O.C. | PCS | 322.69 | 0 | 0 | 322.69 | each | 323 | accesorios.py [DERIVED]: 215.14 LF of exterior bottom track on slab / Inputs!B25 (Expansion anchor spacing (ft) = 0.6667) | 322.6939
Joint compound, all purpose | LB | 1286.84 | 0 | 0 | 1286.84 | lb | 1287 | accesorios.py [DERIVED]: Inputs!B23 (Joint compound (lb per SF) = 0.072) x 17872.8 SF of board | 1286.8416
Joint tape, paper | LF | 6612.93 | 0 | 0 | 6612.93 | LF | 6613 | accesorios.py [DERIVED]: Inputs!B24 (Joint tape (LF per SF) = 0.37) x 17872.8 SF of board | 6612.936
Level 5 finish | SF | 859.27 | 0.06 | 51.5562 | 910.8262 | SF | 911 | accesorios.py [CRITERION]: 1/A11.04 11'-9 1/4" V.I.F.; A00.40 WC-18 'WALL SURFACE TO BE LEVEL 5'; A05.01 key note 12 circle; 6/A11.01 11'-9 1/4" V.I.F.; A00.40 WC-18 'WALL SURFACE TO BE LEVEL 5'; A05.01 key note 12 circle; 5/A11.04 11'-9 1/4" V.I.F.; A00.40 WC-18 'WA
Deflection clips at non-load-bearing walls to structure | PCS | 0 | 0 | 0 | 0 | each | 0 | accesorios.py [CRITERION]: S1.11 LIGHT GAUGE STEEL FRAMING note 2 'PROVIDE MANUFACTURER'S STANDARD VERTICAL DEFLECTION CLIPS AT NON-LOAD-BEARING WALLS'; 1/A12.01, 3/A12.01, 4/A12.01 'CONTINUOUS SLIP TRACK'; 8/A12.01, 9/A12.01 'CONT. SLIP TRACK'

## Pending Items
RFI | Question / condition | Delta of each alternative
RFI-ACC-additional-head-track | additional head track: openings with their own box (openings_extra) > 4'-0": do they also take the additional head track of 2/S5.20 HEAD TRACK @ NON LOAD BRG 'ADD FULL LENGTH ADDL HEAD TRACK @ OPNG >4'-0"'? | 100.56 lf
RFI-ACC-stud-reinforcement-mep | stud reinforcement MEP: plates at double-row stud walls: one per cut row (R72.9) vs one per crossing | -11 pcs
RFI-ACC-stud-reinforcement-mep-2 | stud reinforcement MEP: crossings read by hand (not found by mep.cruces): confirm each one on the M / P sheets (R73.5) | 6 pcs
RFI-ACC-stud-reinforcement-mep-3 | stud reinforcement MEP: pipes over 1 in. through the stud web: the penetration detail draws a plate (R73.5) | 11 pcs
RFI-ACC-stud-reinforcement-mep-4 | stud reinforcement MEP: duct / fire damper openings listed outside the registered MEP sweep (R73.5) | 6 pcs
RFI-ACC-gypsum-board-jamb-return | gypsum board jamb return: jamb return width not dimensioned | -40.74 sf
RFI-ACC-expansion-anchors | expansion anchors: untagged parts of piers / boxes (A-EXT-P2, A-EXT-P4) without anchorage in the schedule (R72.8) | 9.41 pcs
RFI-ACC-slab-pins | slab pins: pin spacing: 12" (interior anchorage) vs 16" (fastener schedule) vs 24" (type K box) | 16in: -133.46 pcs; 24in: -266.93 pcs
RFI-ACC-deflection-clips | deflection clips: deflection clips: the general note asks for them at non-load-bearing walls and the partition details draw a slip / deflection track (R73.6) | 799 pcs
RFI-ACC-stud-reinforcement-mep-5 | stud reinforcement MEP: fire dampers (4) and the 10" trunk at Office 106/107 read by hand; pipes > 1" (P-01..P-07, P-09) draw a plate per 6/S5.20 | FD 4 x 1 = +4 pcs; manual duct +1; pipes 8 x 1 = +8 pcs
RFI-ACC-level-5-finish | Level 5 finish: WC-20 (key note 9) extent not drawn in any elevation and WC-20 missing in A00.40 | carried 15.21 x (10.0 - 0.375) = 146.4 SF; if the whole diagonal face incl. ATM surround: 17.46 x 9.625 = 168.1 SF (+21.7)
RFI-ACC-pvc-trim-at-frp | PVC trim at FRP: Women's 114 width 11'-7 1/2" (1/A08.01) vs 11'-8" (A02.01) | +0.083 ft x 2 on perimeter -> +0.33 LF PVC, +0.83 SF FRP
RFI-ACC-deflection-clips-2 | deflection clips: S1.11 note 2 asks for deflection clips and the A12.01 types draw continuous slip track (R73.6) | one clip per full-height stud of walls to structure (accesorios computes)
RFI-ACC-slab-pins-2 | slab pins: A1K/A5K print PAFs @ 2'-0" alternating sides; interior anchorage S5.20 @ 12" | A1K/A5K bottom track LF / 2 - LF / 1
RFI-ACC-extra-framing-atm | extra framing ATM: DU ATM 6/A08.11 prints 2-1/2" studs sistered to the 6" studs; count / height not printed | carried 5 studs x 6'-0" = 30.0 LF (W1 / R78.36); if only the 2 jamb studs: -18.0 LF
RFI-ACC-access-panel | access panel: M general note 16 (M00.01) 'PROVIDE ACCESS PANELS FOR ALL EQUIPMENT, DAMPERS ... ABOVE CEILINGS': only 1 drawn (RCP key note 4); FCU-2 / dampers above GB ceilings (Vestibules, Waiting, Restrooms) may need more | +n panels (not drawn)
RFI-C1 | Carrying channel direction of the suspended GWB ceilings is not printed (no suspended-GWB ceiling detail in the set). Carried E-W for the whole project. | N-S instead of E-W: carrying -3.08 LF, furring 32.06 LF, hanger wire 0.0 LF
RFI-C2 | No suspended GWB ceiling assembly is detailed (furring/carrying/hanger size & spacing). Per E14 / R70.1 the GWB ceilings are carried as furring channel + carrying channel @48" + hanger wire @48". 6/A09.33 (typical trimless fixture, not bubbled on A04.01) shows '3 5/8" METAL STUD FRAMING @ 16" O.C.' -- local detail, does not change the field. | stud_joist instead of furring: furring -815.83 LF, 3-5/8" stud +815.83 LF
RFI-C3 | R-11C / R-11CE: schedule description 12' vs catalog '-20'-0"'. A04.01 draws and labels 12'. Carried 12'. | +64 LF framed openings if 20' fixtures (2 sides x 8' x 4)
RFI-C4 | UU4 (x4, drive-up canopy) scheduled 55'-0" but A04.01 draws 49.18' bars; the drive-up soffit is 55.47' long (fascia to fascia). Carried 55' (+1/4") per 54.1; UU5 50' vs 49.18' drawn. | -46.56 LF framed openings if the drawn 49.18' length governs (UU4)
RFI-C5 | Rough-opening widths not printed for R-11A/R-11C/R-11CE (6/A09.33), UU1-UU6 (4/A09.33 'COORD. W/ FIXTURE CUTSHEET') and slot diffusers (M00.03 'SEE DRAWING'): sides carried (SIDES_ONLY), ends pending. | +2 x W x qty per tag (see framed_openings rfis: LF per inch of width)
RFI-C6 | Drive-up canopy (W): 15/A09.27 labels only spray foam on the wall behind the canopy, no glass-mat sheathing (3/A09.26 & 7/A09.26 label '5/8" GLASS-MAT SHEATHING'). W band carried with sheathing 'none' (R78.13). | +111.52 SF 5/8" glass mat if the W band gets it (56.344 LF x 1.9792 ft)
RFI-C7 | Restrooms 113/114: A04.01 shows 2'x2' diffuser/grille symbols (drawn 12"x12"); M01.01 shows 2'-0" linear slots (75 / 60 CFM). Carried per M01.01 as 2' slot openings (SIDES_ONLY 2 x 2' x 4 = 16 LF). | -16 LF framed openings if 12"x12" grilles (fit the 16" module)
RFI-C8 | Cash Window 116 CSR soffit: GB 8'-0" strip 3'-5" x 12'-0" between ACT-4 9'-0" fields. No detail is bubbled on A04.01 or on the enlarged RCP 4/A12.08; carried per R70.1 as a suspended furring ceiling with the typical transitions 7/A09.33 on its edges. The set nevertheless details this soffit as stud framing: 9/A12.08 CSR LINE SECTION ('3 5/8" METAL STUDS AT 16" O.C.', bubbled on 1, 2, 5, 6/A12.08) and 10/A09.33 CEILING DETAIL @ CSR SOFFIT (studs to deck both faces, CONT. TRACK, no kickers, no hangers). Confirm the system. | framed soffit (10/A09.33) instead of furring + transitions: furring -48.04 LF, carrying -13.64 LF, hanger wire -59.0 LF (8 pcs x 7.375), kickers -105.44 LF 3-5/8", soffit bottom joists +37.52 LF 3-5/8" @ 16" (11 x 3.411); vertical studs to deck and ceiling track unchanged; net 3-5/8" stud about -67.9 LF
RFI-C9 | S2.20 labels B.O.D. 15'-4 1/2" NO SLOPE only in the F-E bay; E-B bay has no B.O.D. label (beams at grid B and D marked (high), leader '@ LOW ROOF' near grid E between grids 5-6 refers to a steel support). Waiting 104 and the north part of the cash strip carried at 15'-4 1/2". | if E-B were the low roof (13'-0 5/8"): waiting hanger drop 4.375 -> 2.052 ft and transition vertical studs 4.375 -> 2.052 ft (-2.323 ft per piece)
RFI-C10 | Low roof B->A slopes 13'-0 5/8" -> 12'-6 3/8"; restrooms 113/114 and the south cash strip carried at the high end (HEIGHT DE DECK). | -15.62 LF hanger wire if the low end governs
RFI-C11 | Canopy fascia box stud spacing not printed (3/A09.26, 7/A09.26, 16/A09.27); carried 16" o.c. from 5/A09.33 '3 5/8" CFMF @ 16" O.C.' (same canopy assembly). | @24" instead: about -1/3 of fascia studs
RFI-C12 | Canopy soffit joist direction carried perpendicular to the building wall (studs drawn wall->fascia in 3/A09.26); drive-up canopy W (55' x 21') could run N-S between the W12x19 / W10x12 steel. | rotated joists: 3-5/8" stud 212.33 LF
RFI-X1 | Exterior elevation titles are swapped N/S: bubble 1/A09.01 (called from the NORTH edge, looking south) is titled 'SOUTH ELEVATION' but shows the north facade (grid order 8..1, storefront entry); bubble 2/A09.02 (called from the SOUTH edge, looking north) is titled 'NORTH ELEVATION' but shows the south facade (grid order 1..8, door 123). Facades assigned by the north arrow (R71.1). Confirm titles. | 0 (assignment only)
RFI-X2 | Parapet roof-side face: wall sections A09.21-A09.23 label '5/8" EXTERIOR GYPSUM SHEATHING' while 4/A09.26 labels 'FULLY ADHERED ROOF MEMBRANE ON 5/8" DENS DECK OR EQUAL'. Carried as 5/8" exterior gypsum sheathing (53.5 / 55.3). Confirm whether the cover board is by the roofer. | - 954.9 SF exterior gyp sheathing if by roofer
RFI-X3 | Canopy beams (S2.20 '(CANOPY)' W12x19 / W16x26, T/STEEL 11'-9" to 12'-2 3/4") are drawn inside the 6" stud plane in sections A/B/C (A09.21), D/E (A09.22) and H/J (A09.23), below the roof perimeter beam. Studs carried full height to the roof perimeter beam (10/S5.10, 6/S5.10). Alternative: studs stop under the canopy beam and a second short row runs from the canopy beam to the roof beam (two more track runs per wall). | if split at the canopy beam (E26 strict reading, ADV_ext #1, DERIVED from studs_out): about -188 to -206 LF 600S162-54 (each affected stud loses d of the canopy beam: N1 -14.2, E1 -47 to -58, W3A -35.3, W2 -22.4 to -28.8, WJ -8.1, SC-N-VEST -12.2, SC-N-CZ -27.5, SC-W-VEST -10.5, P2+P4 -11) and +321 LF 600T track (deflection + bottom track at the canopy beam on 160.5 LF of affected lines)
RFI-X4 | Roof step at grid B (4/A02.02): row heights are not dimensioned; measured in vector at 1 1/2" = 1'-0". The two T/STEEL lines in the detail are 29.3" apart vs 27.875" from the S2.20 B.O.D. values (5 %). | +/- 5 % of 3 rows x 52.33 ft (about +/- 0.4 ft per row height)
RFI-X5 | Storefront pier jamb strips: label '3/4" FRT PLYWOOD' (singular) but 1/A09.25 and 2/A09.25 draw two 3/4" plies at each storefront jamb. Carried 1 ply (label). | + 23.59 SF 3/4" FRT plywood if 2 plies
RFI-X7 | Exterior 6" CFMF part of the storefront piers: anchorage of its bottom track not stated (R72.8). | anchors vs pins on 2 x (3.375 + 2.896) ft of bottom track
RFI-X8 | Drive-up canopy column wraps (5/A09.25): stud gauge and O.C. not printed (16" used); wrap height taken from T/SLAB 0'-0" to the canopy soffit framing B/STUD 10'-7 1/4" (15/A09.27) - the drive lane / island level at the columns is not dimensioned. | per 0.25 ft of height: 4 wraps x 12 studs x 0.25 = 12 LF 3-5/8" stud and 5.67 SF plywood per wrap
RFI-X10 | Plan details 1/A09.25, 2/A09.25, 5/A09.25 and 7/A08.11 are drawn mirrored with respect to A02.01 (grid F above G, D above E; S2.20 revision note 'BUILDING FOOTPRINT MIRRORED NORTH-SOUTH'). Layers and dimensions read from the details, geometry assigned per the plan. Also 1/A08.01 (restrooms 113 / 114 enlarged plan) is rotated 180 degrees relative to A02.01 (doors, WC and Janitor 112 / Storage 117 reversed): toilet-accessory blocking assigned per room; grab bars / TA-3 / TA-5 / TA-9 / TA-10 / TA-17 sit on the inner face of the west exterior wall A-EXT-W3B. | 0
RFI-X11 | High parapet (T.O. PARAPET 2): return of 4.5 ft at grid 4 south of line G read on the roof plan A02.02 (keynote 10) - no dimension printed. | +/- 1 ft x 4.29 ft parapet
RFI-ENS-01 | MR board: reading A-INT placed the two corridor-niche fixtures as lavatories (MR on the niche back wall A-INT-042); 1/A08.01 shows the restroom lavatory and water closet on the chase walls and the niche pair is the high-low drinking fountain. MR carried on the chase faces of A-INT-039 (114) and A-INT-040 (113) only. | if the niche fixtures were lavatories: + MR on A-INT-042 corridor face (same SF moved from regular to MR)
RFI-ENS-02 | Ceiling transition trim: 7/A09.33 draws a shadow molding at the upper ceiling too (upper condition). Carried 2 corner bead + 1 shadow molding per LF; if the upper shadow molding also applies (ACT side) add 1 LF per LF. | +101.05 LF metal trim (transitions 101.05 LF x 1)
RFI-ENS-03 | DU ATM recess: 6/A08.11 prints '2 1/2" METAL STUD SISTERED TO 6" METAL STUD W/ MINERAL WOOL INSULATION' without count or spacing. Carried 5 studs across the 4'-6" surround x 6'-0" = 30 LF (more material, 53.3). If only the two jambs are sistered: 12 LF. | -18.0 LF extra framing ATM recess (2-1/2" stud) if only 2 jambs
RFI-ENS-04 | Cash Window 116 GB ceiling crosses the deck break at grid B. Hanger wire carried with the high drop (7.375 ft) for all hangers; south half hangs from the low deck (13'-0 5/8" - 8'-0" = 5.052 ft). | about half of the 116 hangers at 5.052 ft instead of 7.375 ft: -2.32 LF per hanger in the low half
RFI-ENS-05 | Storefront pier exterior 6" CFMF L: 1/A09.25 and 2/A09.25 print partial stud chains (carried 3.375 LF NW pier, 2.8958 LF NE pier). Alternative = finished plan L 2'-6 3/4" + 1'-11 3/4" = 4.4583 LF per pier. | +1.0833 LF (A-EXT-P2) / +1.5625 LF (A-EXT-P4) of 6" CFMF pier part
RFI-REF-01 | Fascia box: the details also draw a plywood layer on TOP of the box and part of its back face; only the outer face and the bottom (R78.14) are carried. Top / back plywood extent is not labeled separately. | +71.5 SF 5/8" ext. grade FRT plywood if the top of the box is sheathed (same width as the bottom, 237.595 LF of fascia)
RFI-REF-02 | Exterior walls that own the building corner (A-EXT-S1 W end, A-EXT-S2 E end, A-EXT-N1 E end, A-EXT-WJ W end) carry their interior board face to the OUTER corner (board_caras: sum of face pieces = wall length). The room face physically stops at the inner face of the crossing exterior wall (0.88-0.97 ft per end). | -51.5 SF 5/8" board (S1 -0.887 x 12.5313, S2 -0.880 x 12.5313, N1 -0.967 x 15.375, WJ -0.942 x 15.375) and -3.67 LF sealant at base of gypsum if the faces stop at the inner corner
RFI-REF-03 | High parapet on grid 2 north of the vestibule storefront: the coping runs continuous from line G down grid 2 (A02.02), but A-PP-W-2 sums only its base walls A-EXT-W2 + A-EXT-SC-W-VEST (W2 / R78.37); the west leg of the NW pier (vertical 318.66-337.5 pt on A02.01) is not under any base wall of the W facade. | +1.05 to +1.98 LF parapet x 4.2917 = +4.5 to +8.5 SF 5/8" exterior gyp sheathing (roof side) and the same LF of FRT blocking x plies
RFI-REF-04 | Recessed accessories without a printed size: TA-13 hand dryer with ADA recess kit (x2, drawn 17.2" wide on A/A08.01, more than a 16" bay), FEC-1 recessed extinguisher cabinet (A00.40) and TA-2 recessed paper towel dispensers (x2, Break 118 / Wellness 115). Carried 0 (R71.6 / R60.5); 58.4 asks header + sill at 2'-0" PENDING when not printed. | TA-13: +5.53 LF header and +5.53 LF sill track (2 x (1.433 + 1.333)); FEC-1 + TA-2 x2 at 2'-0": +10.0 LF header and +10.0 LF sill track (3 x (2.0 + 1.333))
RFI-REF-05 | 8/A12.10 DETAIL @ WALL TERMINATION is bubbled only at the west end of VEST-S (3/A12.10); carried there (FRT blocking 10.0 LF). The glass also ends against the 1'-0" C1 box A-INT-049 at the east end of VEST-S and the south end of VEST-E (no bubble). The 'FRT PLYWOOD' behind the 5/8" gyp in 8/A12.10 has no width (break lines). | +20.0 LF FRT blocking if 8/A12.10 applies at the two C1-box ends; FRT plywood +10.0 SF per foot of width per termination
RFI-REF-06 | S1.10 general note 7: 'DELEGATED STRUCTURAL DESIGN AND DEFERRED SUBMITTALS INCLUDE: ... 2. COLD FORMED STEEL FRAMING'; S1.11 light gauge notes ask for supplier shop drawings. CFS delegated design, PE-stamped calculations and shop drawings: confirm whether they are in the framing bid. | 0 in quantities; engineering / submittal cost item (Clarifications)
RFI-REF-07 | 8/S5.20 MECH. CHASE FRAMING IN WALL (toe-to-toe stud posts each side, 1'-10" max, cold rolled channel; plumbing chases 4'-0" apart min.) is not bubbled on the plans; the P01.01 pipes on A-EXT-N1 / A-EXT-E1 cross the walls (mep.cruces), no vertical riser inside a stud wall is drawn. Not carried. | per vertical chase in a 6" exterior wall: +2 studs x 14.36 = +28.7 LF 600S162-54 + about 1.83 LF cold rolled channel per row (PENDING: count of risers in walls, P03.01)
RFI-REF-08 | E02.02 key note 29: 'PROVIDE 8'x7'-6"x3/4" FIRE-RATED PLYWOOD BACKBOARDS MOUNTED VERTICALLY ALONG NER ROOM WALL SHOWN'. Carried per the architectural drawings: 7'-6" long (A02.01) x 7'-6" high (5/A11.03, 6" AFF). 'BACKBOARDS' is plural; the key-note tag is not located as text on E02.02. | +3.75 SF 3/4" FRT plywood if the 8' side runs along the wall; +60 SF per additional 8' x 7'-6" board on another NER wall
RFI-REF-09 | 12/A09.27 SECTION DETAIL @ STUCCO BASE: 'CEMENT BOARD ON RIGID INSULATION' on the foundation face below T/BASE 0'-6". Taken as foundation / insulation work by others (not carried). | if included: LF of stucco walls x (1'-2" + depth to footing, not printed) of cement board
RFI-REF-10 | Edge-of-gypboard stud blocking 4/S5.20 (NTS, no location, REGLA 56.8 / 59.14): carried (b) one row on every face whose board piece exceeds the 12 ft sheet = 560.96 LF 362CR22 (53.3). | (a) exterior walls + double-layer types (G, G1, A1K, B2K) only = 425.60 LF: -135.36 LF metal stud blocking
RFI-REF-11 | A08.01 key note 8 'GC TO MOUNT THE MIRROR TO THE FACE OF GYPSUM BOARD AND PROVIDE FRP AROUND THE MIRROR'S HOUSING' (TA-7, Men's 113 and Women's 114): the mirror rises above the 5'-0" FRP (elevation A/A08.01). Strip width and mirror height are not dimensioned; not carried (the FRP schema has only the 5'-0" perimeter and the mop sink). | per mirror (2): FRP = (2 x h + w) x strip width above 5'-0" + PVC edge trim on both edges; with the drawn 2'-0" wide mirror and a 4" strip about +1.8 SF FRP and +11 LF PVC trim per mirror (PENDING: not printed)
RFI-REF-12 | A12.04 labels the shelving blocking of MW05 / MW06 / MW08 'PROVIDE ADDITIONAL PRESSURE TREATED BLOCKING IN PARTITION' while sheet note D (A12.03-A12.06) says 'PROVIDE FRTW BLOCKING AT ALL MILLWORK VERTICAL SURFACE CLEATS AND MOUNTING LOCATIONS'. Carried as FRT blocking. | material only, same LF (pressure-treated wood instead of FRTW on the MW05 / MW06 / MW08 rows)
RFI-INT-01 | Tag 'B2K' (PC0011) at the north end of the teller line is not in the A12.01 schedule. Taken as the 6" ballistic type = A5K row of 4/A12.01 (6" stud, 7 5/8", 14 ga @ 24", 5/8" + 3/8" level-2 fiberglass to 8'-0" + 3/8" gyp above): measured 7.68" = 7 5/8" and the K family adds 3/8" (B2 7 1/4" + 3/8"). | if plain B2 instead: -13.9 SF ballistic panel, -12.8 SF 3/8" gyp; studs 20 ga @16" instead of 14 ga @24" on 1.74 LF
RFI-INT-02 | Customer side of the teller-line K walls is not labeled on plan; taken as the side away from the teller area (north wall: north face; south wall: south face). The north A1K (PT0011) customer face sits in a 3.3" closed cavity against the G wall (A02.01 vector 1115.76 / 1120.68 pt). | no quantity change if reversed (same face length); confirm panel side and the cavity
RFI-INT-03 | G / G1 (5/A12.01) board drawn above the scheduled ceiling without a top dimension; taken to deck (9/A12.01 office-front note '2 LAYERS ... TO EXTEND TO UNDERSIDE OF DECK', 53.3). Data: the three G1 bands (A-INT-004, A-INT-006, A-INT-032) measure 12.72 pt = 8.48" on A02.01 vs 8" in the A12.01 schedule (the type governs; length unchanged). | if board stops at ceiling + 6": -2249.8 SF 5/8" board (2 layers each face)
RFI-INT-04 | C1 (6/A12.01) and the C1 boxes (3/A08.21, A09.25) have no top dimension (break line); studs and board taken to deck (60.11 / 53.3). | if board stops at the room ceiling + 6": -195.2 SF 5/8" board; MR alternative (ADV_int #4): chase faces A-INT-039 / 040 MR only up to ceiling + 6" and regular above: -78.4 SF MR / +78.4 SF regular (by face: 013 group -43.9, 025 -10.2, 049 -18.0, 050 -10.9, 051 -19.7, 052 -15.3 SF regular if C1 stops at ceiling + 6")
RFI-INT-05 | Vestibule heads VEST-HEAD-S / VEST-HEAD-E: 'METAL STUD FRAMING & BOX HEADER AS NEEDED' without stud size or box size; 3-5/8" @ 16" assumed, studs from the head (10'-0") to deck; VEST-E Central Zone face board taken to deck. | VEST-E board to Central Zone ceiling + 6" (12'-0") instead of deck: -21.7 SF
RFI-INT-06 | Wall A-INT-044 (B2, Women's 114 / Corridor) crosses the grid-B deck break 0.45 ft south of its north end; door 114's north jamb is 0.8" north of grid B. Split at grid B (D9): A-INT-044a 0.4467 ft at 15'-4 1/2" (high), A-INT-044b 5.095 ft at 13'-0 5/8" (low high end); door 114 in A-INT-044b. | whole wall at the high-zone B.O.D. 15'-4 1/2" instead: +11.84 SF per face (+23.7 SF 5/8" board) and about +2.32 LF per 6" stud of A-INT-044b
RFI-INT-07 | Grille 103 head elevation not dimensioned (A00.30 HEIGHT 13'-6 1/2" conflicts with ceilings); head framing length taken from the 4/A08.21 chain 1'-6" + 2'-4 1/2" (independent of the elevation). | none for the head framing; affects only the vendor opening
RFI-INT-08 | Office front CONT. BOX BEAM depth not printed (8/9/A12.01); bulkhead studs counted from the head to deck (box depth not subtracted, 53.3). | per 1" of box depth: -0.0833 ft x stud count of each bulkhead
RFI-INT-09 | Opening-table data check for the A-OPEN task: plan bubble '111' is the door in the corridor north wall (gap 1160.4-1220.4 pt, vertical 1229-1236) and '122' is the door in the corridor east wall (1253.76-1313.76 pt); the table xy_pt of 111 / 122 are swapped. VEST-S printed chain 4'-9 1/2" + 6'-2" + 4'-8 1/4" adds to 15'-7 3/4" (15.6458), the table carries 15'-8". | VEST-S header +/- 0.0208 ft x 4 pieces; 111 / 122 refs placed by the plan bubbles (heads 8.1667 / 7.1667 copied from the table rows)
RFI-INT-10 | Candidate tag PA0034 'B' (smaller symbol) inside the janitor closet is counted on the Janitor 112 / Storage 117 wall A-INT-047 (thickness 4.88" = B / A1). | if A1 (default) instead of B: board stops at ceiling + 6" -> both rooms are open to structure, so no board change; type count moves 3.5 LF B -> A1
RFI-INT-11 | Walls only partly under an S2.20 beam (or under two candidate beams): studs carried to deck over the whole length: A-INT-003 (two parallel beams with different marks within 1 ft of the band (W12X19 3.015 ft, W12X19 3.015 ft, W8X10 3.82 ft)); A-INT-005 (beam W8X10 covers only 3.36 ft = 28.9 % of the wall); A-INT-032 (beam W8X10 covers only 3.354 ft = 28.5 % of the wall); A-INT-037 (beam W14X30 covers only 1.795 ft = 55.2 % of the wall); A-INT-046 (beam W8X10 covers only 5.287 ft = 45.1 % of the wall); A-INT-048 (beam (unlabeled) covers only 5.287 ft = 45.1 % of the wall) | per wall: covered length x beam depth (d) of studs and board
RFI-FO-01 | RFI R-11C: opening width not printed (6/A09.33); confirm R-11C/R-11CE rough opening width (Focal Point FSM2L trimless) - ends not carried; ends not carried | +2 x W x 2 LF (ends; W pending); 0.3333 LF per inch of opening width
RFI-FO-02 | RFI R-11CE: opening width not printed (6/A09.33); confirm R-11CE rough opening width - ends not carried; ends not carried | +2 x W x 2 LF (ends; W pending); 0.3333 LF per inch of opening width
RFI-FO-03 | RFI R-11A: opening width not printed (6/A09.33); confirm R-11A rough opening width - ends not carried; ends not carried | +2 x W x 2 LF (ends; W pending); 0.3333 LF per inch of opening width
RFI-FO-04 | RFI UU1: opening width not printed (4/A09.33); confirm UU1 rough opening width (Coronet LSR-WET-2.5) - ends not carried; ends not carried | +2 x W x 1 LF (ends; W pending); 0.1667 LF per inch of opening width
RFI-FO-05 | RFI UU2: opening width not printed (4/A09.33); confirm UU2 rough opening width (Coronet LSR-WET-2.5) - ends not carried; ends not carried | +2 x W x 5 LF (ends; W pending); 0.8333 LF per inch of opening width
RFI-FO-06 | RFI UU3: opening width not printed (4/A09.33); confirm UU3 rough opening width (Coronet LSR-WET-2.5) - ends not carried; ends not carried | +2 x W x 9 LF (ends; W pending); 1.5 LF per inch of opening width
RFI-FO-07 | RFI UU4: opening width not printed (4/A09.33); confirm UU4 rough opening width (Coronet LSR-WET-2.5) - ends not carried; ends not carried | +2 x W x 4 LF (ends; W pending); 0.6667 LF per inch of opening width
RFI-FO-08 | RFI UU5: opening width not printed (4/A09.33); confirm UU5 rough opening width (Coronet LSR-WET-2.5) - ends not carried; ends not carried | +2 x W x 1 LF (ends; W pending); 0.1667 LF per inch of opening width
RFI-FO-09 | RFI UU6: opening width not printed (4/A09.33); confirm UU6 rough opening width (Coronet LSR-WET-2.5) - ends not carried; ends not carried | +2 x W x 1 LF (ends; W pending); 0.1667 LF per inch of opening width
RFI-FO-10 | RFI SD-VEST: opening width not printed (M00.03); confirm slot diffuser (SD / TBDI-10) section rough opening width in GWB - ends not carried; ends not carried | +2 x W x 12 LF (ends; W pending); 2 LF per inch of opening width
RFI-FO-11 | RFI SD-RR: opening width not printed (M00.03); confirm restroom slot diffuser rough opening width; A04.01 shows 2'x2' diffuser symbols at these points (RFI-C7); ends not carried | +2 x W x 4 LF (ends; W pending); 0.6667 LF per inch of opening width
RFI-SCOPE-CL1 | RFI: confirm 7/8" hat channel @ 16" O.C. under EPS-5 metal panel (cladding substrate) - not quantified, by cladding installer (A09.26, A09.27, 1/A09.31, 2/A09.31, 3/A09.25) is cladding substrate by the cladding installer, excluded from metal frame / drywall scope; | n/a: cladding substrate not measured (by the cladding installer); if included, quantify it over the EPS-5 metal panel areas (A09.26, A09.27, 1/A09.31, 2/A09.31, 3/A09.25)
RFI-SCOPE-CL2 | RFI: confirm self-furring metal lath under 7/8" cement plaster / stucco (cladding substrate) - not quantified, by plaster installer (A09.26, A09.27, 5/A09.31, 6/A09.31) is cladding substrate by the cladding installer, excluded from metal frame / drywall scope; | n/a: cladding substrate not measured (by the cladding installer); if included, quantify it over the stucco areas (A09.26, A09.27, 5/A09.31, 6/A09.31)
RFI-COR-01 | Bracing: 123.04 LF of C.R. channel run across openings without studs (53.4 literal, corridas_out.json) | -123.04 LF bracing C.R. channel if it is not run across openings
RFI-COR-02 | Bottom track: 50.5 LF of door rough openings are NOT deducted from the bottom track (corridas_out.json) | -50.5 LF bottom track if door R.O. are deducted
RFI-PEND-01 | equipment mounted on walls (A00.40 equipment schedule: combo/cork boards, wall clock, wall-mount phones #24, monitor arms, FMX-12 dispenser ...): A02.01 note C obliges blocking; the A11.02 items (Break, Work, Wellness, Calling Cubes) are carried in BLK-EQ. Still open: items on the office elevations A11.01 / A11.03 / A11.04 (#7 combo boards, #9 clocks, #3 hooks, #111 monitor arms) - one row of metal stud blocking per item once counted | n/a: blocking at wall-mounted equipment not located on plan; add 1 row of metal stud blocking per item once located (not carried)
RFI-OPEN-01 | SF-AF2-N-CZ head detail is not called by any section; read as 2/A09.26 (steel header framing, S2.20 HSS9x5x5/8 on that line). If 11/A09.27 governs instead, a metal stud box beam applies. | +4 x (26.25 + 1.333) = +110.33 LF header / box beam
RFI-OPEN-02 | Teller (CSR) line 12'-0 1/4" R.O. HOLD: no header printed and the span exceeds the 7/S5.20 maximum of 8'-0"; carried 0 LF (R71.10). | +26.71 LF (2-362CSJ20) or +53.42 LF (4-piece box)
RFI-OPEN-03 | DU ATM R.O.: 7/A08.11 gives 2'-2 1/2" and 5/A08.11 gives 2'-2 1/8"; sill and head are dimensioned from the finished drive lane (slab-to-lane offset not printed). | 0.125 in on the R.O. (about 0.04 LF header / sill track)
RFI-OPEN-04 | Type A door R.O. sits exactly at the SINGLE TRACK limit of the 7/S5.20 header schedule (3'-4" = row maximum); a larger field R.O. moves the row to DOUBLE TRACK. | +4.67 LF per door, 13 doors = +60.7 LF header
RFI-REV-01 | B2K / A1K type-change block (A02.01, teller line north wall): the hatched Z block x 1653.96-1661.76 pt is carried in A1K A-INT-027 (printed 3'-5"); resolution item 12 gave it to B2K A-INT-026 (2.2067 LF). | B2K +0.4334 LF, A1K -0.4333 LF if the block is B2K
RFI-REV-02 | Corner bead at the office-front bulkheads (TR-01) carried on both bottom edges of each bulkhead box (2 x 45.0 LF of openings = 90.0 LF, 8/A12.01, 9/A12.01). | -45.0 LF metal trim if only one edge per opening

## Review Items
41 questions in total, asked ONE at a time in this order: floor plan (partition types A-Z), then the details the floor plan calls, in order
# | Phase | Type / order | Item | Sheet + detail | Image
1/41 | Floor plan | A1K | RFI-INT-02: Customer side of the teller-line K walls is not labeled on plan; taken as the side away from the teller area (north wall: north face; south wall: south face). The north A1K (PT0011) customer face sits in a 3.3" closed cavity against the G wall (A02.01 vector 1115.76 / 1120.68 pt). ¦ Delta: no quantity change if reversed (same face length); confirm panel side and the cavity | 4/A12.01 TELLER SIDE / CUSTOMER SIDE | /home/user/boa27b/work/etapas/2_lectura/A/img/int/W_A-INT-027.png
2/41 | Floor plan | B | RFI-INT-10: Candidate tag PA0034 'B' (smaller symbol) inside the janitor closet is counted on the Janitor 112 / Storage 117 wall A-INT-047 (thickness 4.88" = B / A1). ¦ Delta: if A1 (default) instead of B: board stops at ceiling + 6" -> both rooms are open to structure, so no board change; type count moves 3.5 LF B -> A1 | A02.01 | /home/user/boa27b/work/etapas/2_lectura/A/img/int/W_A-INT-047.png
3/41 | Floor plan | B2 | RFI-INT-06: Wall A-INT-044 (B2, Women's 114 / Corridor) crosses the grid-B deck break 0.45 ft south of its north end; door 114's north jamb is 0.8" north of grid B. Split at grid B (D9): A-INT-044a 0.4467 ft at 15'-4 1/2" (high), A-INT-044b 5.095 ft at 13'-0 5/8" (low high end); door 114 in A-INT-044b. ¦ Delta: whole wall at the high-zone B.O.D. 15'-4 1/2" instead: +11.84 SF per face (+23.7 SF 5/8" board) and about +2.32 LF per 6" stud of A-INT-044b | S2.20 | /home/user/boa27b/work/etapas/2_lectura/A/img/int/W_A-INT-044.png
4/41 | Floor plan | B2K | RFI-INT-01: Tag 'B2K' (PC0011) at the north end of the teller line is not in the A12.01 schedule. Taken as the 6" ballistic type = A5K row of 4/A12.01 (6" stud, 7 5/8", 14 ga @ 24", 5/8" + 3/8" level-2 fiberglass to 8'-0" + 3/8" gyp above): measured 7.68" = 7 5/8" and the K family adds 3/8" (B2 7 1/4" + 3/8"). ¦ Delta: if plain B2 instead: -13.9 SF ballistic panel, -12.8 SF 3/8" gyp; studs 20 ga @16" instead of 14 ga @24" on 1.74 LF | A02.01 tag B2K + 4/A12.01 | /home/user/boa27b/work/etapas/2_lectura/A/img/int/W_A-INT-026.png
5/41 | Floor plan | B2K | RFI-REV-01: B2K / A1K type-change block (A02.01, teller line north wall): the hatched Z block x 1653.96-1661.76 pt is carried in A1K A-INT-027 (printed 3'-5"); resolution item 12 gave it to B2K A-INT-026 (2.2067 LF). ¦ Delta: B2K +0.4334 LF, A1K -0.4333 LF if the block is B2K | A02.01; 4/A12.01 | /home/user/boa27b/work/etapas/3_revision/img_res/03_12_zoom_type_change.png
6/41 | Floor plan | BULKHEAD-G | RFI-REV-02: Corner bead at the office-front bulkheads (TR-01) carried on both bottom edges of each bulkhead box (2 x 45.0 LF of openings = 90.0 LF, 8/A12.01, 9/A12.01). ¦ Delta: -45.0 LF metal trim if only one edge per opening | 8/A12.01; 9/A12.01
7/41 | Floor plan | BULKHEAD-G | RFI-INT-08: Office front CONT. BOX BEAM depth not printed (8/9/A12.01); bulkhead studs counted from the head to deck (box depth not subtracted, 53.3). ¦ Delta: per 1" of box depth: -0.0833 ft x stud count of each bulkhead | 8/A12.01, 9/A12.01, 7/A11.01, 8/A11.01 | /home/user/boa27b/work/etapas/2_lectura/A/img/int/det_9_8_A1201.png
8/41 | Floor plan | C1 | RFI-INT-04: C1 (6/A12.01) and the C1 boxes (3/A08.21, A09.25) have no top dimension (break line); studs and board taken to deck (60.11 / 53.3). ¦ Delta: if board stops at the room ceiling + 6": -195.2 SF 5/8" board; MR alternative (ADV_int #4): chase faces A-INT-039 / 040 MR only up to ceiling + 6" and regular above: -78.4 SF MR / +78.4 SF regular (by face: 013 group -43.9, 025 -10.2, 049 -18.0, 050 -10.9, 051 -19.7, 052 -15.3 SF regular if C1 stops at ceiling + 6") | 6/A12.01 | /home/user/boa27b/work/etapas/2_lectura/A/img/int/det_6_A1201.png
9/41 | Floor plan | CANOPY-COL | RFI-X8: Drive-up canopy column wraps (5/A09.25): stud gauge and O.C. not printed (16" used); wrap height taken from T/SLAB 0'-0" to the canopy soffit framing B/STUD 10'-7 1/4" (15/A09.27) - the drive lane / island level at the columns is not dimensioned. ¦ Delta: per 0.25 ft of height: 4 wraps x 12 studs x 0.25 = 12 LF 3-5/8" stud and 5.67 SF plywood per wrap | 5/A09.25, 15/A09.27 | /home/user/boa27b/work/etapas/2_lectura/A/img/ext/A0925_5.png
10/41 | Floor plan | EXT-6CFMF | RFI-ENS-05: Storefront pier exterior 6" CFMF L: 1/A09.25 and 2/A09.25 print partial stud chains (carried 3.375 LF NW pier, 2.8958 LF NE pier). Alternative = finished plan L 2'-6 3/4" + 1'-11 3/4" = 4.4583 LF per pier. ¦ Delta: +1.0833 LF (A-EXT-P2) / +1.5625 LF (A-EXT-P4) of 6" CFMF pier part | 1/A09.25; 2/A09.25 | /home/user/boa27b/work/etapas/3_revision/img_res/07_13_1-A09.25_storefront_pier_grid2.png
11/41 | Floor plan | EXT-6CFMF | RFI-X3: Canopy beams (S2.20 '(CANOPY)' W12x19 / W16x26, T/STEEL 11'-9" to 12'-2 3/4") are drawn inside the 6" stud plane in sections A/B/C (A09.21), D/E (A09.22) and H/J (A09.23), below the roof perimeter beam. Studs carried full height to the roof perimeter beam (10/S5.10, 6/S5.10). Alternative: studs stop under the canopy beam and a second short row runs from the canopy beam to the roof beam (two more track runs per wall). ¦ Delta: if split at the canopy beam (E26 strict reading, ADV_ext #1, DERIVED from studs_out): about -188 to -206 LF 600S162-54 (each affected stud loses d of the canopy beam: N1 -14.2, E1 -47 to -58, W3A -35.3, W2 -22.4 to -28.8, WJ -8.1, SC-N-VEST -12.2, SC-N-CZ -27.5, SC-W-VEST -10.5, P2+P4 -11) and +321 LF 600T track (deflection + bottom track at the canopy beam on 160.5 LF of affected lines) | S2.20, A09.21-A09.23, 10/S5.10 | /home/user/boa27b/work/etapas/2_lectura/A/img/ext/A0923_H_canopy.png
12/41 | Floor plan | EXT-6CFMF | RFI-X7: Exterior 6" CFMF part of the storefront piers: anchorage of its bottom track not stated (R72.8). ¦ Delta: anchors vs pins on 2 x (3.375 + 2.896) ft of bottom track | 1/A09.25, 2/A09.25, S1.11 | /home/user/boa27b/work/etapas/2_lectura/A/img/ext/A0925_2.png
13/41 | Floor plan | EXT-PARAPET | RFI-X11: High parapet (T.O. PARAPET 2): return of 4.5 ft at grid 4 south of line G read on the roof plan A02.02 (keynote 10) - no dimension printed. ¦ Delta: +/- 1 ft x 4.29 ft parapet | A02.02 | /home/user/boa27b/work/etapas/2_lectura/A/img/ext/roof_NW.png
14/41 | Floor plan | EXT-PARAPET | RFI-X2: Parapet roof-side face: wall sections A09.21-A09.23 label '5/8" EXTERIOR GYPSUM SHEATHING' while 4/A09.26 labels 'FULLY ADHERED ROOF MEMBRANE ON 5/8" DENS DECK OR EQUAL'. Carried as 5/8" exterior gypsum sheathing (53.5 / 55.3). Confirm whether the cover board is by the roofer. ¦ Delta: - 954.9 SF exterior gyp sheathing if by roofer | C/A09.21, 4/A09.26 | /home/user/boa27b/work/etapas/2_lectura/A/img/ext/A0926_4.png
15/41 | Floor plan | G | RFI-INT-03: G / G1 (5/A12.01) board drawn above the scheduled ceiling without a top dimension; taken to deck (9/A12.01 office-front note '2 LAYERS ... TO EXTEND TO UNDERSIDE OF DECK', 53.3). Data: the three G1 bands (A-INT-004, A-INT-006, A-INT-032) measure 12.72 pt = 8.48" on A02.01 vs 8" in the A12.01 schedule (the type governs; length unchanged). ¦ Delta: if board stops at ceiling + 6": -2249.8 SF 5/8" board (2 layers each face) | 5/A12.01, 9/A12.01 | /home/user/boa27b/work/etapas/2_lectura/A/img/int/det_5_A1201.png
16/41 | Floor plan | G | RFI-INT-11: Walls only partly under an S2.20 beam (or under two candidate beams): studs carried to deck over the whole length: A-INT-003 (two parallel beams with different marks within 1 ft of the band (W12X19 3.015 ft, W12X19 3.015 ft, W8X10 3.82 ft)); A-INT-005 (beam W8X10 covers only 3.36 ft = 28.9 % of the wall); A-INT-032 (beam W8X10 covers only 3.354 ft = 28.5 % of the wall); A-INT-037 (beam W14X30 covers only 1.795 ft = 55.2 % of the wall); A-INT-046 (beam W8X10 covers only 5.287 ft = 45.1 % of the wall); A-INT-048 (beam (unlabeled) covers only 5.287 ft = 45.1 % of the wall) ¦ Delta: per wall: covered length x beam depth (d) of studs and board | S2.20 | /home/user/boa27b/work/etapas/2_lectura/A/img/int/W_A-INT-005.png
17/41 | Detail | 1 | RFI-X1: Exterior elevation titles are swapped N/S: bubble 1/A09.01 (called from the NORTH edge, looking south) is titled 'SOUTH ELEVATION' but shows the north facade (grid order 8..1, storefront entry); bubble 2/A09.02 (called from the SOUTH edge, looking north) is titled 'NORTH ELEVATION' but shows the south facade (grid order 1..8, door 123). Facades assigned by the north arrow (R71.1). Confirm titles. ¦ Delta: 0 (assignment only) | 1/A09.01 | /home/user/boa27b/work/etapas/2_lectura/A/img/ext/callouts_4.png
18/41 | Detail | 2 | RFI-INT-09: Opening-table data check for the A-OPEN task: plan bubble '111' is the door in the corridor north wall (gap 1160.4-1220.4 pt, vertical 1229-1236) and '122' is the door in the corridor east wall (1253.76-1313.76 pt); the table xy_pt of 111 / 122 are swapped. VEST-S printed chain 4'-9 1/2" + 6'-2" + 4'-8 1/4" adds to 15'-7 3/4" (15.6458), the table carries 15'-8". ¦ Delta: VEST-S header +/- 0.0208 ft x 4 pieces; 111 / 122 refs placed by the plan bubbles (heads 8.1667 / 7.1667 copied from the table rows) | 1/A12.10 | /home/user/boa27b/work/etapas/2_lectura/A/img/int/W_A-INT-008.png
19/41 | Detail | 3 | RFI-OPEN-03: DU ATM R.O.: 7/A08.11 gives 2'-2 1/2" and 5/A08.11 gives 2'-2 1/8"; sill and head are dimensioned from the finished drive lane (slab-to-lane offset not printed). ¦ Delta: 0.125 in on the R.O. (about 0.04 LF header / sill track) | 7/A08.11
20/41 | Detail | 4 | RFI-ENS-01: MR board: reading A-INT placed the two corridor-niche fixtures as lavatories (MR on the niche back wall A-INT-042); 1/A08.01 shows the restroom lavatory and water closet on the chase walls and the niche pair is the high-low drinking fountain. MR carried on the chase faces of A-INT-039 (114) and A-INT-040 (113) only. ¦ Delta: if the niche fixtures were lavatories: + MR on A-INT-042 corridor face (same SF moved from regular to MR) | 1/A08.01 | /home/user/boa27b/work/etapas/2_lectura/A/img/acc/A0801_1_plan.png
21/41 | Detail | 4 | RFI-ACC-pvc-trim-at-frp: PVC trim at FRP: Women's 114 width 11'-7 1/2" (1/A08.01) vs 11'-8" (A02.01) ¦ Delta: +0.083 ft x 2 on perimeter -> +0.33 LF PVC, +0.83 SF FRP | 1/A08.01
22/41 | Detail | 5 | RFI-X4: Roof step at grid B (4/A02.02): row heights are not dimensioned; measured in vector at 1 1/2" = 1'-0". The two T/STEEL lines in the detail are 29.3" apart vs 27.875" from the S2.20 B.O.D. values (5 %). ¦ Delta: +/- 5 % of 3 rows x 52.33 ft (about +/- 0.4 ft per row height) | 4/A02.02 | /home/user/boa27b/work/etapas/2_lectura/A/img/ext/A0202_4.png
23/41 | Detail | 6 | RFI-ENS-03: DU ATM recess: 6/A08.11 prints '2 1/2" METAL STUD SISTERED TO 6" METAL STUD W/ MINERAL WOOL INSULATION' without count or spacing. Carried 5 studs across the 4'-6" surround x 6'-0" = 30 LF (more material, 53.3). If only the two jambs are sistered: 12 LF. ¦ Delta: -18.0 LF extra framing ATM recess (2-1/2" stud) if only 2 jambs | 6/A08.11 | /home/user/boa27b/work/etapas/2_lectura/A/img/acc/A0811_6_DU_section.png
24/41 | Detail | 7 | RFI-INT-07: Grille 103 head elevation not dimensioned (A00.30 HEIGHT 13'-6 1/2" conflicts with ceilings); head framing length taken from the 4/A08.21 chain 1'-6" + 2'-4 1/2" (independent of the elevation). ¦ Delta: none for the head framing; affects only the vendor opening | 4/A08.21 | /home/user/boa27b/work/etapas/2_lectura/A/img/open/A0821_4_grille_head.png
25/41 | Detail | 8 | RFI-X5: Storefront pier jamb strips: label '3/4" FRT PLYWOOD' (singular) but 1/A09.25 and 2/A09.25 draw two 3/4" plies at each storefront jamb. Carried 1 ply (label). ¦ Delta: + 23.59 SF 3/4" FRT plywood if 2 plies | 1/A09.25 | /home/user/boa27b/work/etapas/2_lectura/A/img/ext/A0925_1z.png
26/41 | Detail | 8 | RFI-X10: Plan details 1/A09.25, 2/A09.25, 5/A09.25 and 7/A08.11 are drawn mirrored with respect to A02.01 (grid F above G, D above E; S2.20 revision note 'BUILDING FOOTPRINT MIRRORED NORTH-SOUTH'). Layers and dimensions read from the details, geometry assigned per the plan. Also 1/A08.01 (restrooms 113 / 114 enlarged plan) is rotated 180 degrees relative to A02.01 (doors, WC and Janitor 112 / Storage 117 reversed): toilet-accessory blocking assigned per room; grab bars / TA-3 / TA-5 / TA-9 / TA-10 / TA-17 sit on the inner face of the west exterior wall A-EXT-W3B. ¦ Delta: 0 | 1/A09.25 | /home/user/boa27b/work/etapas/2_lectura/A/img/ext/A0925_1.png
27/41 | Detail | 9 | RFI-OPEN-01: SF-AF2-N-CZ head detail is not called by any section; read as 2/A09.26 (steel header framing, S2.20 HSS9x5x5/8 on that line). If 11/A09.27 governs instead, a metal stud box beam applies. ¦ Delta: +4 x (26.25 + 1.333) = +110.33 LF header / box beam | 2/A09.26 | /home/user/boa27b/work/etapas/2_lectura/A/img/open/A0821_4_grille_head.png
28/41 | Detail | 10 | RFI-C11: Canopy fascia box stud spacing not printed (3/A09.26, 7/A09.26, 16/A09.27); carried 16" o.c. from 5/A09.33 '3 5/8" CFMF @ 16" O.C.' (same canopy assembly). ¦ Delta: @24" instead: about -1/3 of fascia studs | 3/A09.26 | /home/user/boa27b/work/etapas/2_lectura/A/img/ceil/d3_A0926.png
29/41 | Detail | 10 | RFI-C12: Canopy soffit joist direction carried perpendicular to the building wall (studs drawn wall->fascia in 3/A09.26); drive-up canopy W (55' x 21') could run N-S between the W12x19 / W10x12 steel. ¦ Delta: rotated joists: 3-5/8" stud 212.33 LF | 3/A09.26 | /home/user/boa27b/work/etapas/2_lectura/A/img/ceil/d3_A0926.png
30/41 | Detail | 11 | RFI-ACC-gypsum-board-jamb-return: gypsum board jamb return: jamb return width not dimensioned ¦ Delta: -40.74 sf | 11/A09.27
31/41 | Detail | 12 | RFI-C6: Drive-up canopy (W): 15/A09.27 labels only spray foam on the wall behind the canopy, no glass-mat sheathing (3/A09.26 & 7/A09.26 label '5/8" GLASS-MAT SHEATHING'). W band carried with sheathing 'none' (R78.13). ¦ Delta: +111.52 SF 5/8" glass mat if the W band gets it (56.344 LF x 1.9792 ft) | 15/A09.27 | /home/user/boa27b/work/etapas/2_lectura/A/img/ceil/d15_A0927.png
32/41 | Detail | 13 | RFI-C5: Rough-opening widths not printed for R-11A/R-11C/R-11CE (6/A09.33), UU1-UU6 (4/A09.33 'COORD. W/ FIXTURE CUTSHEET') and slot diffusers (M00.03 'SEE DRAWING'): sides carried (SIDES_ONLY), ends pending. ¦ Delta: +2 x W x qty per tag (see framed_openings rfis: LF per inch of width) | 6/A09.33 | /home/user/boa27b/work/etapas/2_lectura/A/img/ceil/d6_A0933.png
33/41 | Detail | 14 | RFI-C8: Cash Window 116 CSR soffit: GB 8'-0" strip 3'-5" x 12'-0" between ACT-4 9'-0" fields. No detail is bubbled on A04.01 or on the enlarged RCP 4/A12.08; carried per R70.1 as a suspended furring ceiling with the typical transitions 7/A09.33 on its edges. The set nevertheless details this soffit as stud framing: 9/A12.08 CSR LINE SECTION ('3 5/8" METAL STUDS AT 16" O.C.', bubbled on 1, 2, 5, 6/A12.08) and 10/A09.33 CEILING DETAIL @ CSR SOFFIT (studs to deck both faces, CONT. TRACK, no kickers, no hangers). Confirm the system. ¦ Delta: framed soffit (10/A09.33) instead of furring + transitions: furring -48.04 LF, carrying -13.64 LF, hanger wire -59.0 LF (8 pcs x 7.375), kickers -105.44 LF 3-5/8", soffit bottom joists +37.52 LF 3-5/8" @ 16" (11 x 3.411); vertical studs to deck and ceiling track unchanged; net 3-5/8" stud about -67.9 LF | 7/A09.33 | /home/user/boa27b/work/Back-check/img_acc/F1_A1208_sec9_rcp4.png
34/41 | Detail | 14 | RFI-ENS-02: Ceiling transition trim: 7/A09.33 draws a shadow molding at the upper ceiling too (upper condition). Carried 2 corner bead + 1 shadow molding per LF; if the upper shadow molding also applies (ACT side) add 1 LF per LF. ¦ Delta: +101.05 LF metal trim (transitions 101.05 LF x 1) | 7/A09.33 | /home/user/boa27b/work/etapas/2_lectura/A/img/ceil/d7_A0933.png
35/41 | Detail | 15 | RFI-ACC-deflection-clips: deflection clips: deflection clips: the general note asks for them at non-load-bearing walls and the partition details draw a slip / deflection track (R73.6) ¦ Delta: 799 pcs | 1/A12.01
36/41 | Detail | 16 | RFI-ACC-slab-pins: slab pins: pin spacing: 12" (interior anchorage) vs 16" (fastener schedule) vs 24" (type K box) ¦ Delta: 16in: -133.46 pcs; 24in: -266.93 pcs | 11/A12.01
37/41 | Detail | 17 | RFI-INT-05: Vestibule heads VEST-HEAD-S / VEST-HEAD-E: 'METAL STUD FRAMING & BOX HEADER AS NEEDED' without stud size or box size; 3-5/8" @ 16" assumed, studs from the head (10'-0") to deck; VEST-E Central Zone face board taken to deck. ¦ Delta: VEST-E board to Central Zone ceiling + 6" (12'-0") instead of deck: -21.7 SF | 7/A12.10 | /home/user/boa27b/work/etapas/2_lectura/A/img/int/A1210_5_4_heads.png
38/41 | Detail | 18 | RFI-ACC-additional-head-track: additional head track: openings with their own box (openings_extra) > 4'-0": do they also take the additional head track of 2/S5.20 HEAD TRACK @ NON LOAD BRG 'ADD FULL LENGTH ADDL HEAD TRACK @ OPNG >4'-0"'? ¦ Delta: 100.56 lf | 2/S5.20
39/41 | Detail | 19 | RFI-ACC-stud-reinforcement-mep: stud reinforcement MEP: plates at double-row stud walls: one per cut row (R72.9) vs one per crossing ¦ Delta: -11 pcs | 6/S5.20
40/41 | Detail | 20 | RFI-OPEN-02: Teller (CSR) line 12'-0 1/4" R.O. HOLD: no header printed and the span exceeds the 7/S5.20 maximum of 8'-0"; carried 0 LF (R71.10). ¦ Delta: +26.71 LF (2-362CSJ20) or +53.42 LF (4-piece box) | 7/S5.20
41/41 | Detail | 20 | RFI-OPEN-04: Type A door R.O. sits exactly at the SINGLE TRACK limit of the 7/S5.20 header schedule (3'-4" = row maximum); a larger field R.O. moves the row to DOUBLE TRACK. ¦ Delta: +4.67 LF per door, 13 doors = +60.7 LF header | 7/S5.20

## Scope Checklist
Scope ID | Scope | Status | Note (quantity, NOT APPLICABLE + sheet, or RFI)
ALC-01 | Interior partition framing (studs + tracks) | QUANTIFIED | Partition Takeoff (types A1, A1K, A5, B, B2, B2K, C1, F, G, G1); 3-5/8" stud 6994.55 LF, 1-5/8" stud 3847.86 LF; 1/A12.01, 3/A12.01, 5/A12.01
ALC-02 | Exterior wall framing (CFMF) | QUANTIFIED | EXT-6CFMF 215.14 LF; 6" stud 4656.26 LF; 5/A09.26
ALC-03 | Parapet framing | QUANTIFIED | EXT-PARAPET 269.14 LF; 6" parapet stud 1001.46 LF; 4/A09.26; S5.10
ALC-04 | Top / deflection and bottom track | QUANTIFIED | bottom track 1352.11 LF and top / deflection track 1352.11 LF by stud size (R71.8); deflection clips 0 + RFI (S1.11 note 2 vs continuous slip track 1/A12.01)
ALC-05 | Headers, sills and jambs at openings | QUANTIFIED | header / box beam 796.79 LF, sill track 119.12 LF, additional head track 56 LF, jamb return 67.91 SF; 7/S5.20, 2/S5.20, 11/A09.27
ALC-06 | Bracing / bridging | QUANTIFIED | bracing 1-1/2" C.R. channel 2509.27 LF (corridas_out.json); S5.20
ALC-07 | Gypsum board on walls (layers per type) | QUANTIFIED | 5/8" gypsum board regular 17548.3 SF (walls by face, board_out.json + ceilings); A12.01
ALC-08 | Moisture / abuse / special board at wet zones | QUANTIFIED | 5/8" moisture resistant gypsum board 258.87 SF behind the restroom fixtures; 1/A08.01, A08.01 note F
ALC-09 | Exterior gypsum / glass mat sheathing | QUANTIFIED | 5/8" glass mat sheathing 362.16 SF; 5/8" exterior gypsum sheathing 952.24 SF; 5/A09.26, 4/A09.26
ALC-10 | FRT plywood sheathing / substrate | QUANTIFIED | FRT plywood 6705.03 SF by material and use (frt_plywood_by_material); A09.26, A11.03
ALC-11 | Gypsum board ceilings | QUANTIFIED | suspended gypsum board ceilings by room (A04.01 'NEW SUSPENDED GYPSUM WALL BOARD'), board inside the 5/8" regular row; RFI-C1, RFI-C2
ALC-12 | Ceiling suspension (furring / carrying channel / hanger wire / ceiling track) | QUANTIFIED | furring channel 815.83 LF, carrying channel 336.03 LF, hanger wire 592.63 LF (121 hangers), ceiling / soffit track 1244.13 LF; A04.01
ALC-13 | Soffits and bulkheads (framing + board) | QUANTIFIED | office-front bulkheads BULKHEAD-G 45 LF (9/A12.01), vestibule heads (7/A12.10, 5/A12.10), ceiling transitions (7/A09.33): OTHER FRAMING rows
ALC-14 | Canopy / marquee framing and sheathing | QUANTIFIED | canopy fascia boxes and soffit joists (3/A09.26, 7/A09.26, 16/A09.27), FRT plywood canopy sheathing and column wraps (frt_plywood_by_material), CANOPY-COL 22.67 LF (5/A09.25)
ALC-15 | Column furring / wraps | QUANTIFIED | interior column boxes C1 (3/A08.21, 1/A09.25, 2/A09.25) and drive-up canopy column wraps CANOPY-COL 22.67 LF (5/A09.25)
ALC-16 | Blocking (FRT wood / metal) for millwork and accessories | QUANTIFIED | FRT blocking 989.85 LF; metal stud blocking 603.94 LF (edge of gypboard 4/S5.20 + wall-mounted items); RFI-PEND-01
ALC-17 | Framed openings (MEP, access panels, diffusers) | QUANTIFIED | framed openings MEP 918.88 LF (framed_openings_out.json, ends pending RFI-FO); access panel 1 PCS (A04.01 key note 4); M00.01 / P00.01 legends only
ALC-18 | Trim: corner bead, casing bead, control joints, reveals | QUANTIFIED | metal trim (corner bead, casing bead, shadow molding) 1052.1 LF (A12.01, A09.33, A08.21). No gypsum board control joint is labeled or detailed: A00.00 abbreviation only, A09.01 / A09.22 / A09.31 are stucco control joints, p17 and S3.20 are pavement / slab joints; reveals A09.26 are ACM
ALC-19 | Acoustical sealant / sound attenuation (EXCLUDED: estimator standing order, all projects) | NOT APPLICABLE | EXCLUDED: EXCLUDED in all projects (estimator standing order): no acoustical sealant row and no quantity
ALC-20 | FRP / cement board / tile backer | QUANTIFIED | FRP 334.75 SF, cement board 31.88 SF, PVC trim at FRP 223.5 LF; A08.01
ALC-21 | Shaft walls / area separation walls | NOT APPLICABLE | NOT APPLICABLE: no shaft wall or area separation wall in the A12.01 partition schedule or on A02.01 (scan found no mention in the set)
ALC-22 | Rated assemblies (UL designs) and their board type | NOT APPLICABLE | NOT APPLICABLE: no rated partition and no UL design in the A12.01 schedule; 'FIRE RATED' on A11.03 / E02.02 is the 3/4" fire-rated plywood backboard (carried in FRT plywood), A12.02 is the NER paint note, M00.01 / M03.01 / E00.01 are generic penetration notes and E04.02 is a firestop detail
ALC-23 | Special panels (ballistic, lead-lined, abuse) | QUANTIFIED | ballistic panel 85.34 SF (A1K / A5K / B2K, 4/A12.01 '3/8" UL752 LISTED LEVEL-2 FIBERGLASS'); 3/8" gypsum board 65.65 SF
ALC-24 | Finish level (Level 4 / Level 5) | QUANTIFIED | Level 5 finish 859.27 SF (A00.40 WC-18 / WC-22, A05.01 key notes; A08.11, A12.02 WC-20)
ALC-X25 | batt insulation | NOT APPLICABLE | EXCLUDED (estimator criterion: no insulation)

## _reglas (hidden)
reglas.py compuerta OK
{"canon": "b8d8bba8e711f71f6b99faf76e67912722678d2034f762d6a94d112038b2a6b5", "evidencias": "0d063403618da9c8aef89767ed2b74b557f7974a79647d2c0a59b8248c99da08", "familias_out": "692263d1ce585822763cc34e1260a2286a0accf0121b7e0388721eae5d16b756", "reglas": "177a49c3146aaf8f9e5137cc871673167657f0d0a37fd7a5e09230365bdcedce", "version": "v73"}