## Inputs
BOA Broomfield (bank branch), Broomfield CO ¦ METAL FRAMING & DRYWALL TAKEOFF
Bid set: boa.pdf · 2026-10-21 · Edit ONLY the yellow cells.
PARAMETER | VALUE | NOTE / SOURCE
Waste - ALL METAL, any type | 0.15 | Estimator standing rule: 15% on everything that is metal.
Waste - EVERYTHING THAT IS NOT METAL | 0.06 | Estimator standing rule: same figure as board.
Board sheet width (ft) | 4 | Sheet size is a parameter; buy the size that wastes least.
Board sheet length (ft) | 12 | Change it and every sheet count re-rounds.
SF per board sheet | 48 | Width x length.
Stud stock length (ft) | 20 | Stud, header, framed opening and stud blocking: sticks.
Track stock length (ft) | 10 | Track, sill track and purlin: runs.
Floor plan scale (pt/ft) | 18 | Project value (canon constants).
B.O. Deck (ft) | 15.375 | Project value (canon constants).
T.O. Parapet (ft) | n/a | Project value (canon constants).
Sealant coverage (LF per tube) | 25 | Sealant yield per tube - set your supplier's figure.
C.R. channel stock length (ft) | 16 | 1-1/2" cold-rolled channel (bracing, carrying channel).
Hat / furring channel stock (ft) | 12 | 7/8" hat furring channel.
Trim stick length (ft) | 10 | Corner bead, casing bead, shadow molding, PVC trim.
Hanger wire purchase | continuous coil (LF) | Bought by LF from a continuous coil; the hanger count goes on its own PCS row.
Drywall screws per SF of board | 1.2 | YIELD (GA-216 field / perimeter spacing).
Framing screws per stud piece | 4 | YIELD: 2 per stud-to-track connection, each end.
Power-driven pin spacing (ft) | 1 | YIELD: bottom track on slab, interior walls.
Joint compound (lb per SF) | 0.072 | YIELD: 72 lb per 1,000 SF, level 4 (estimator criterion).
Joint tape (LF per SF) | 0.37 | YIELD: 370 LF per 1,000 SF.
Expansion anchor spacing (ft) | 0.6667 | YIELD: exterior bottom track on slab.

## Partition Takeoff
ORGANIZED PARTITION TAKEOFF - BOA Broomfield (bank branch), Broomfield CO
Grouped by partition type. Every row cites its DETAIL/SHEET and its status.
Partition / Scope | Wall # | Length (LF) | Height (FT) | Layers | Stud Size | Stud O.C. (in) | Board (SF) | Location | Source (DETAIL/SHEET) | Status
TYPE A1
A1 #A1-01 - N wall of CALLING CUBES 122 (and over MW01 alcove), from W end at MW01 cabinet opening to E outer face of A5 wall A1-14 | A1-01 | 17.02 | 15.375 | 2 | 3-5/8" | 16 | 366.95 | N wall of CALLING CUBES 122 (and over MW01 alcove), from W end at MW01 cabinet opening to E outer face of A5 wall A1-14 | 3/A12.01 | [DERIVED]
A1 #A1-02 - E wall of MW01 alcove / W side of CALLING CUBES 122 north part | A1-02 | 3.125 | 15.375 | 2 | 3-5/8" | 16 | 76.17 | E wall of MW01 alcove / W side of CALLING CUBES 122 north part | 3/A12.01 | [DERIVED]
A1 #A1-03 - S wall of MW01 alcove (jog between A5 wall A1-15 and A1-02) | A1-03 | 2.427 | 15.375 | 2 | 3-5/8" | 16 | 59.16 | S wall of MW01 alcove (jog between A5 wall A1-15 and A1-02) | 3/A12.01 | [DERIVED]
A1 #A1-04 - N end wall of CORRIDOR 111 with door 111, from E face of restroom 114 B2/G1 wall to W face of A5 wall A1-15 | A1-04 | 5.587 | 15.375 | 2 | 3-5/8" | 16 | 62.88 | N end wall of CORRIDOR 111 with door 111, from E face of restroom 114 B2/G1 wall to W face of A5 wall A1-15 | 3/A12.01 | [DERIVED]
A1 #A1-05 - S wall of CALLING CUBES 122 / N wall of BREAK ROOM 118 (MW21 against S face), from jamb box at doors 122/118B to A5 wall A1-14 | A1-05 | 15.833 | 12.965 | 2 | 3-5/8" | 16 | 285 | S wall of CALLING CUBES 122 / N wall of BREAK ROOM 118 (MW21 against S face), from jamb box at doors 122/118B to A5 wall A1-14 | 3/A12.01 | [DERIVED]
A1 #A1-06 - N wall of BREAK ROOM 118 with door 118A, from W outer face of A1-07 to W face of A5 A1-17 | A1-06 | 5.5 | 12.921 | 2 | 3-5/8" | 16 | 47.31 | N wall of BREAK ROOM 118 with door 118A, from W outer face of A1-07 to W face of A5 A1-17 | 3/A12.01 | [DERIVED]
A1 #A1-07 - Short wall S of A5 A1-14, E edge of MW21 area (between CALLING CUBES 122 SE corner and N wall of BREAK ROOM 118) | A1-07 | 1.733 | 11.819 | 2 | 3-5/8" | 16 | 32.06 | Short wall S of A5 A1-14, E edge of MW21 area (between CALLING CUBES 122 SE corner and N wall of BREAK ROOM 118) | 3/A12.01 | [DERIVED]
A1 #A1-08 - E wall of CORRIDOR 111 / W wall of BREAK ROOM 118 arm, ELECTRICAL 120 and NER 121, with door 118B, from S face of A1-05 to S exterior wall | A1-08 | 20.521 | 11.819 | 2 | 3-5/8" | 16 | 360.9 | E wall of CORRIDOR 111 / W wall of BREAK ROOM 118 arm, ELECTRICAL 120 and NER 121, with door 118B, from S face of A1-05 to S exterior wall | 3/A12.01 | [DERIVED]
A1 #A1-09 - N wall of WORK ROOM 119 / S wall of CASH WINDOW 116, with door 119, from E face of B2 wall (x 1633.08) to inner face of E exterior wall (x 1843.08) | A1-09 | 11.667 | 12.768 | 2 | 3-5/8" | 16 | 168.06 | N wall of WORK ROOM 119 / S wall of CASH WINDOW 116, with door 119, from E face of B2 wall (x 1633.08) to inner face of E exterior wall (x 1843.08) | 3/A12.01 | [DERIVED]
TYPE A1K
A1K #A1-11 - S face of OFFICE 4 CB 108 G wall: N teller-line wall of CASH WINDOW 116 (ballistic), x 1653.96-1715.40 | A1-11 | 3.417 | 15.375 | 1 | 3-5/8" | 24 | 52.54 | S face of OFFICE 4 CB 108 G wall: N teller-line wall of CASH WINDOW 116 (ballistic), x 1653.96-1715.40 | 4/A12.01 | [DERIVED]
A1K #A1-12 - S ballistic wall W part: between A5 A1-17 top and the jog at x 1653.96 (N side of FUTURE FCAM area) | A1-12 | 1.767 | 12.92 | 2 | 3-5/8" | 24 | 45.66 | S ballistic wall W part: between A5 A1-17 top and the jog at x 1653.96 (N side of FUTURE FCAM area) | 4/A12.01 | [DERIVED]
A1K #A1-13 - S ballistic wall E part of teller line (CASH WINDOW 116), x 1653.96-1715.40, above FUTURE FCAM C1 box | A1-13 | 3.413 | 12.932 | 2 | 3-5/8" | 24 | 88.28 | S ballistic wall E part of teller line (CASH WINDOW 116), x 1653.96-1715.40, above FUTURE FCAM C1 box | 4/A12.01 | [DERIVED]
TYPE A5
A5 #A1-14a+A1-14b - E wall of CALLING CUBES 122, from S face of A1-01 to S face of A1-05 (bottom y 1324.08) | A1-14a+A1-14b | 19.406 | 13.707 | 2 | 6" | 16 | 378.39 | E wall of CALLING CUBES 122, from S face of A1-01 to S face of A1-05 (bottom y 1324.08) | 3/A12.01 | [DERIVED]
A5 #A1-15 - W wall of CALLING CUBES 122 (S of MW01 alcove), with recessed FEC-1 on the W face, from S face of A1-03 down to N wall of corridor (bottom y 1236.36) | A1-15 | 14.127 | 15.375 | 2 | 6" | 16 | 265.81 | W wall of CALLING CUBES 122 (S of MW01 alcove), with recessed FEC-1 on the W face, from S face of A1-03 down to N wall of corridor (bottom y 1236.36) | 3/A12.01 | [DERIVED]
A5 #A1-16a+A1-16b - Short A5 jamb wall at SW corner of CALLING CUBES 122 (jogged E of A1-15) with door 122, down to N face of A1-05 | A1-16a+A1-16b | 4.873 | 12.578 | 2 | 6" | 16 | 39.94 | Short A5 jamb wall at SW corner of CALLING CUBES 122 (jogged E of A1-15) with door 122, down to N face of A1-05 | 3/A12.01 | [DERIVED]
A5 #A1-17 - W wall of FUTURE FCAM area / E wall of BREAK ROOM 118 N part, with door 116, from S face of A1K A1-12 to top of B2 wall PT0027 (y 1482.12) | A1-17 | 6.947 | 11.774 | 2 | 6" | 16 | 80.74 | W wall of FUTURE FCAM area / E wall of BREAK ROOM 118 N part, with door 116, from S face of A1K A1-12 to top of B2 wall PT0027 (y 1482.12) | 3/A12.01 | [DERIVED]
TYPE B
B #A2-B-01 - N wall of ELECTRICAL 120 (S side of BREAK ROOM 118), between A1 corridor wall (x 1241.8) and B wall A2-B-06 | A2-B-01 | 9.99 | 12.825 | 2 | 3-5/8" | 16 | 256.24 | N wall of ELECTRICAL 120 (S side of BREAK ROOM 118), between A1 corridor wall (x 1241.8) and B wall A2-B-06 | 1/A12.01 | [DERIVED]
B #A2-B-02 - S wall of MEN'S RESTROOM 113 / N wall of JANITOR CLOSET 112 and STORAGE 117, west exterior wall to corridor B2 wall A2-B2-03 | A2-B-02 | 11.719 | 12.087 | 2 | 3-5/8" | 16 | 235.52 | S wall of MEN'S RESTROOM 113 / N wall of JANITOR CLOSET 112 and STORAGE 117, west exterior wall to corridor B2 wall A2-B2-03 | 1/A12.01 | [DERIVED]
B #A2-B-03 - Wall between JANITOR CLOSET 112 (MW06A) and STORAGE 117 (MW05), between A2-B-02 and A2-B-04 | A2-B-03 | 3.5 | 12.741 | 2 | 3-5/8" | 16 | 89.18 | Wall between JANITOR CLOSET 112 (MW06A) and STORAGE 117 (MW05), between A2-B-02 and A2-B-04 | 1/A12.01 | [DERIVED]
B #A2-B-04 - S wall of JANITOR CLOSET 112 and STORAGE 117 / N wall of WELLNESS 115, west exterior wall to corridor B2 wall A2-B2-03 (two tags on one line) | A2-B-04 | 11.719 | 12.664 | 2 | 3-5/8" | 16 | 296.82 | S wall of JANITOR CLOSET 112 and STORAGE 117 / N wall of WELLNESS 115, west exterior wall to corridor B2 wall A2-B2-03 (two tags on one line) | 1/A12.01 | [DERIVED]
B #A2-B-05 - Wall between ELECTRICAL 120 and NER 121, A1 corridor wall (x 1241.8) to B wall A2-B-06 | A2-B-05 | 9.583 | 12.696 | 2 | 3-5/8" | 16 | 243.34 | Wall between ELECTRICAL 120 and NER 121, A1 corridor wall (x 1241.8) to B wall A2-B-06 | 1/A12.01 | [DERIVED]
B #A2-B-06 - E wall of ELECTRICAL 120 and NER 121 (W side of BREAK ROOM 118), from A2-B-01 to south exterior wall | A2-B-06 | 13.74 | 12.821 | 2 | 3-5/8" | 16 | 256.76 | E wall of ELECTRICAL 120 and NER 121 (W side of BREAK ROOM 118), from A2-B-01 to south exterior wall | 1/A12.01 | [DERIVED]
TYPE B2
B2 #A2-B2-01 - E wall of ATM ROOM 102 (door 102), from C1 column wrap A2-C1-04 down to G wall A2-G-01 | A2-B2-01 | 5.667 | 15.375 | 2 | 6" | 16 | 111.66 | E wall of ATM ROOM 102 (door 102), from C1 column wrap A2-C1-04 down to G wall A2-G-01 | 1/A12.01 | [DERIVED]
B2 #A2-B2-02a+A2-B2-02b - E wall of WOMEN'S RESTROOM 114 (door 114) / W side of CORRIDOR 111, from G wall line y 1236.4 to the lavatory alcove top return | A2-B2-02a+A2-B2-02b | 5.542 | 13.275 | 2 | 6" | 16 | 99.36 | E wall of WOMEN'S RESTROOM 114 (door 114) / W side of CORRIDOR 111, from G wall line y 1236.4 to the lavatory alcove top return | 1/A12.01 | [DERIVED]
B2 #A2-B2-03 - Corridor west wall: E wall of MEN'S RESTROOM 113, STORAGE 117 and WELLNESS 115 (doors 113, 117, 115), from the lavatory alcove bottom return to the south exterior wall (two tags on one line) | A2-B2-03 | 15.787 | 12.863 | 2 | 6" | 16 | 262.8 | Corridor west wall: E wall of MEN'S RESTROOM 113, STORAGE 117 and WELLNESS 115 (doors 113, 117, 115), from the lavatory alcove bottom return to the south exterior wall (two tags on one line) | 1/A12.01 | [DERIVED]
B2 #A2-B2-04 - Wall between BREAK ROOM 118 and WORK ROOM 119, from A1 wall (y 1488.1) to south exterior wall (two tags on one line) | A2-B2-04 | 11.407 | 11.631 | 2 | 6" | 16 | 265.34 | Wall between BREAK ROOM 118 and WORK ROOM 119, from A1 wall (y 1488.1) to south exterior wall (two tags on one line) | 1/A12.01 | [DERIVED]
TYPE B2K
B2K #A2-B2K-01 - Kevlar wall at SW corner of OFFICE 4 CB 108 (S of office front), between front-line stub A2-G-11 and the A1K jog | A2-B2K-01 | 1.5 | 15.375 | 2 | 6" | 24 | 46.12 | Kevlar wall at SW corner of OFFICE 4 CB 108 (S of office front), between front-line stub A2-G-11 and the A1K jog | 4/A12.01 | [DERIVED]
TYPE C1
C1 #A2-C1-01 - NW storefront pier of VESTIBULE 100 (grid 2 / F-G), C1 interior framing faces | A2-C1-01 | 3.267 | 15.375 | 1 | 3-5/8" | 16 | 50.23 | NW storefront pier of VESTIBULE 100 (grid 2 / F-G), C1 interior framing faces | 1/A09.25 | [DERIVED]
C1 #A2-C1-02 - NE storefront pier of VESTIBULE 100 (grid 4 / F-G), C1 interior framing faces | A2-C1-02 | 4.073 | 15.375 | 1 | 3-5/8" | 16 | 62.63 | NE storefront pier of VESTIBULE 100 (grid 4 / F-G), C1 interior framing faces | 2/A09.25 | [DERIVED]
C1 #A2-C1-03 - 1'-0" x 1'-0" column wrap at E end of the VESTIBULE 100 / 24 HR VESTIBULE 101 line (door 101), storefront glazing above and below | A2-C1-03 | 4 | 15.375 | 1 | 3-5/8" | 16 | 61.52 | 1'-0" x 1'-0" column wrap at E end of the VESTIBULE 100 / 24 HR VESTIBULE 101 line (door 101), storefront glazing above and below | 6/A12.01 | [DERIVED]
C1 #A2-C1-04 - 1'-0" x 1'-0" column wrap at E end of the diagonal F wall (24 HR VESTIBULE 101 / ATM ROOM 102), storefront glazing above | A2-C1-04 | 2.94 | 15.375 | 1 | 3-5/8" | 16 | 45.21 | 1'-0" x 1'-0" column wrap at E end of the diagonal F wall (24 HR VESTIBULE 101 / ATM ROOM 102), storefront glazing above | 6/A12.01 | [DERIVED]
C1 #A2-C1-05+A2-C1-05E+A2-C1-05W - C1 furring on N side of the CALLING CUBES 122 A1 wall (display monitor keynote 7), facing WAITING 104 + return of the C1 furring A2-C1-05 (R73.17) | A2-C1-05+A2-C1-05E+A2-C1-05W | 11.334 | 15.375 | 1 | 3-5/8" | 16 | 174.27 | C1 furring on N side of the CALLING CUBES 122 A1 wall (display monitor keynote 7), facing WAITING 104 + return of the C1 furring A2-C1-05 (R73.17) | 6/A12.01 | [DERIVED]
C1 #A2-C1-06 - N furring of the plumbing chase between WOMEN'S RESTROOM 114 and MEN'S RESTROOM 113 (face toward 114) | A2-C1-06 | 10.027 | 12.921 | 1 | 3-5/8" | 16 | 129.56 | N furring of the plumbing chase between WOMEN'S RESTROOM 114 and MEN'S RESTROOM 113 (face toward 114) | 6/A12.01 | [DERIVED]
C1 #A2-C1-07 - S furring of the plumbing chase between WOMEN'S RESTROOM 114 and MEN'S RESTROOM 113 (face toward 113) | A2-C1-07 | 10.027 | 12.89 | 1 | 3-5/8" | 16 | 129.25 | S furring of the plumbing chase between WOMEN'S RESTROOM 114 and MEN'S RESTROOM 113 (face toward 113) | 6/A12.01 | [DERIVED]
C1 #A2-C1-08+A2-C1-08E - C1 furring on S side of the A1K teller wall at 'FUTURE FCAM' (CASH WINDOW 116) + return of the C1 furring A2-C1-08 (R73.17) | A2-C1-08+A2-C1-08E | 3.56 | 12.921 | 1 | 3-5/8" | 16 | 46 | C1 furring on S side of the A1K teller wall at 'FUTURE FCAM' (CASH WINDOW 116) + return of the C1 furring A2-C1-08 (R73.17) | 6/A12.01 | [DERIVED]
TYPE F
F #A2-F-01 - Diagonal wall (60 deg) between 24 HR VESTIBULE 101 and ATM ROOM 102 (DAY 1 ATM), west exterior wall to C1 column wrap A2-C1-04 | A2-F-01 | 17.762 | 15.375 | 2 | 3-5/8" | 16 | 325.38 | Diagonal wall (60 deg) between 24 HR VESTIBULE 101 and ATM ROOM 102 (DAY 1 ATM), west exterior wall to C1 column wrap A2-C1-04 | 12/A12.01 | [DERIVED]
TYPE G
G #A2-G-01 - S wall of ATM ROOM 102 / N wall of OFFICE 5 CB 109, storefront pier (x 911.9) to the west office front line, incl. the 4" return at front 109 | A2-G-01 | 12.333 | 15.375 | 4 | 1-5/8" | 16 | 758.48 | S wall of ATM ROOM 102 / N wall of OFFICE 5 CB 109, storefront pier (x 911.9) to the west office front line, incl. the 4" return at front 109 | 5/A12.01 | [DERIVED]
G #A2-G-02 - Demising wall between OFFICE 5 CB 109 and OFFICE 6 CB 110, west exterior wall to G1 front stub A2-G1-02 | A2-G-02 | 11.625 | 14.717 | 4 | 1-5/8" | 16 | 684.34 | Demising wall between OFFICE 5 CB 109 and OFFICE 6 CB 110, west exterior wall to G1 front stub A2-G1-02 | 5/A12.01 | [DERIVED]
G #A2-G-03 - S wall of OFFICE 6 CB 110 / N wall of WOMEN'S RESTROOM 114, west exterior wall to E face of the west front line | A2-G-03 | 12.332 | 15.375 | 4 | 1-5/8" | 16 | 758.42 | S wall of OFFICE 6 CB 110 / N wall of WOMEN'S RESTROOM 114, west exterior wall to E face of the west front line | 5/A12.01 | [DERIVED]
G #A2-G-04 - East office front line stub between DFC-1A fronts (OFFICE 1 ME 105 / OFFICE 2 CL 106) | A2-G-04 | 3.467 | 14.383 | 4 | 1-5/8" | 16 | 199.46 | East office front line stub between DFC-1A fronts (OFFICE 1 ME 105 / OFFICE 2 CL 106) | 5/A12.01 | [DERIVED]
G #A2-G-05 - East office front line stub between DFC-1A fronts (OFFICE 2 CL 106 / OFFICE 3 SB 107) | A2-G-05 | 3.253 | 14.225 | 4 | 1-5/8" | 16 | 185.1 | East office front line stub between DFC-1A fronts (OFFICE 2 CL 106 / OFFICE 3 SB 107) | 5/A12.01 | [DERIVED]
G #A2-G-06 - East office front line stub between DFC-1A fronts (OFFICE 3 SB 107 / OFFICE 4 CB 108) | A2-G-06 | 3.253 | 14.225 | 4 | 1-5/8" | 16 | 185.1 | East office front line stub between DFC-1A fronts (OFFICE 3 SB 107 / OFFICE 4 CB 108) | 5/A12.01 | [DERIVED]
G #A2-G-07 - Demising wall between OFFICE 2 CL 106 and OFFICE 3 SB 107, east office front line to east exterior wall | A2-G-07 | 11.771 | 15.375 | 4 | 1-5/8" | 16 | 723.92 | Demising wall between OFFICE 2 CL 106 and OFFICE 3 SB 107, east office front line to east exterior wall | 5/A12.01 | [DERIVED]
G #A2-G-08 - Demising wall between OFFICE 3 SB 107 and OFFICE 4 CB 108, east office front line to east exterior wall | A2-G-08 | 11.771 | 15.375 | 4 | 1-5/8" | 16 | 723.92 | Demising wall between OFFICE 3 SB 107 and OFFICE 4 CB 108, east office front line to east exterior wall | 5/A12.01 | [DERIVED]
G #A2-G-09 - S wall of OFFICE 4 CB 108 / N wall of CASH WINDOW 116, from A1K jog (x 1661.8) to east exterior wall | A2-G-09 | 10.073 | 15.375 | 4 | 1-5/8" | 16 | 619.48 | S wall of OFFICE 4 CB 108 / N wall of CASH WINDOW 116, from A1K jog (x 1661.8) to east exterior wall | 5/A12.01 | [DERIVED]
G #A2-G-10 - East office front line, north stub: north exterior wall to front 105 first jamb (OFFICE 1 ME 105) | A2-G-10 | 2.42 | 14.383 | 4 | 1-5/8" | 16 | 139.22 | East office front line, north stub: north exterior wall to front 105 first jamb (OFFICE 1 ME 105) | 5/A12.01 | [DERIVED]
G #A2-G-11 - East office front line, south stub: front 108 last jamb to the B2K corner | A2-G-11 | 0.973 | 15.375 | 4 | 1-5/8" | 16 | 59.84 | East office front line, south stub: front 108 last jamb to the B2K corner | 5/A12.01 | [DERIVED]
TYPE G1
G1 #A2-G1-01 - Demising wall between OFFICE 1 ME 105 and OFFICE 2 CL 106, east office front line to east exterior wall | A2-G1-01 | 11.771 | 14.717 | 4 | 1-5/8" | 16 | 692.94 | Demising wall between OFFICE 1 ME 105 and OFFICE 2 CL 106, east office front line to east exterior wall | 5/A12.01 | [DERIVED]
G1 #A2-G1-02 - West office front line stub between DFC-1A fronts of OFFICE 5 CB 109 and OFFICE 6 CB 110 | A2-G1-02 | 3.507 | 15.375 | 4 | 1-5/8" | 16 | 215.68 | West office front line stub between DFC-1A fronts of OFFICE 5 CB 109 and OFFICE 6 CB 110 | 5/A12.01 | [DERIVED]
G1 #A2-G1-03 - West office front line, south stub: front 110 last jamb to G wall A2-G-03 | A2-G1-03 | 2.667 | 15.375 | 4 | 1-5/8" | 16 | 164.02 | West office front line, south stub: front 110 last jamb to G wall A2-G-03 | 5/A12.01 | [DERIVED]
TYPE BULKHEAD-G
BULKHEAD-G #A2-BH-01+A2-BH-02+A2-BH-03+A2-BH-04 - Office bulkhead over the DFC-1A office front of OFFICE 1 ME 105 (front line east) + Office bulkhead over the DFC-1A office front of OFFICE 2 CL 106 (front line east) + Office bulkhead over the DFC-1A office front of OFFICE 3 SB 107 (front line east) + Office bulkhead over the DFC-1A office front of OFFICE 4 CB 108 (front line east) | A2-BH-01+A2-BH-02+A2-BH-03+A2-BH-04 | 30 | 6.263 | 5 | 1-5/8" | 16 | 770.28 | Office bulkhead over the DFC-1A office front of OFFICE 1 ME 105 (front line east) + Office bulkhead over the DFC-1A office front of OFFICE 2 CL 106 (front line east) + Office bulkhead over the DFC-1A office front of OFFICE 3 SB 107 (front line east) + Office bulkhead over the DFC-1A office front of OFFICE 4 CB 108 (front line east) | 8/A12.01 | [DERIVED]
BULKHEAD-G #A2-BH-05+A2-BH-06 - Office bulkhead over the DFC-1A office front of OFFICE 5 CB 109 (front line west) + Office bulkhead over the DFC-1A office front of OFFICE 6 CB 110 (front line west) | A2-BH-05+A2-BH-06 | 15 | 7.333 | 5 | 1-5/8" | 16 | 449.38 | Office bulkhead over the DFC-1A office front of OFFICE 5 CB 109 (front line west) + Office bulkhead over the DFC-1A office front of OFFICE 6 CB 110 (front line west) | 8/A12.01 | [DERIVED]
TYPE EXT-6CFMF
EXT-6CFMF #A3-N1 - North facade, grid F between storefront east jamb (grid ~7) and NE corner grid 8 (Office 105 north wall) | A3-N1 | 13.187 | 14.358 | 1 | 6" | 16 | 202.75 | North facade, grid F between storefront east jamb (grid ~7) and NE corner grid 8 (Office 105 north wall) | C/A09.21 | [DERIVED]
EXT-6CFMF #A3-E1a+A3-E1b - East facade, grid 8 from NE corner (grid F) to grid B (Offices 105-108, Cash Window 116) + East facade, grid 8 from grid B to SE corner grid A (Work Room 119, Break Room 118 side) | A3-E1a+A3-E1b | 75.44 | 13.549 | 1 | 6" | 16 | 1037.97 | East facade, grid 8 from NE corner (grid F) to grid B (Offices 105-108, Cash Window 116) + East facade, grid 8 from grid B to SE corner grid A (Work Room 119, Break Room 118 side) | C/A09.21 | [DERIVED]
EXT-6CFMF #A3-S1a+A3-S1b - South facade, grid A from SW corner (grid 3) to grid 6 (Wellness 115, door 123 exit, NER 121) + South facade, grid A from grid 6 to SE corner grid 8 (Break Room 118, Work Room 119) | A3-S1a+A3-S1b | 52.834 | 11.171 | 1 | 6" | 16 | 634.86 | South facade, grid A from SW corner (grid 3) to grid 6 (Wellness 115, door 123 exit, NER 121) + South facade, grid A from grid 6 to SE corner grid 8 (Break Room 118, Work Room 119) | C/A09.21 | [DERIVED]
EXT-6CFMF #A3-W2a+A3-W2b - West facade, grid 3 from grid D to grid B (Offices 109 / 110) + West facade, grid 3 from grid B to SW corner grid A (restrooms 113/114, Janitor 112, Wellness 115) | A3-W2a+A3-W2b | 47.427 | 13.071 | 1 | 6" | 16 | 639.27 | West facade, grid 3 from grid D to grid B (Offices 109 / 110) + West facade, grid 3 from grid B to SW corner grid A (restrooms 113/114, Janitor 112, Wellness 115) | C/A09.21 | [DERIVED]
EXT-6CFMF #A3-SJ - South-facing jog at grid D between grid 2 and grid 3 (south wall of ATM Room 102) | A3-SJ | 3.86 | 14.358 | 1 | 6" | 16 | 59.35 | South-facing jog at grid D between grid 2 and grid 3 (south wall of ATM Room 102) | C/A09.21 | [DERIVED]
EXT-6CFMF #A3-W1 - West facade, grid 2 from storefront south jamb (Vestibule 100) to outside corner 2/D (24 HR Vestibule 101, ATM Room 102) | A3-W1 | 21.462 | 14.358 | 1 | 6" | 16 | 321.54 | West facade, grid 2 from storefront south jamb (Vestibule 100) to outside corner 2/D (24 HR Vestibule 101, ATM Room 102) | C/A09.21 | [DERIVED]
EXT-6CFMF #A3-PIER2 - A3-PIER2 | A3-PIER2 | 4.542 | 14.358 | 0 | 6" CFMF (600S162-54) | 16 | 0 | A3-PIER2 | 1/A09.25 (plan A02.01) | [DERIVED]
EXT-6CFMF #A3-PIER4 - A3-PIER4 | A3-PIER4 | 3.984 | 14.358 | 0 | 6" CFMF (600S162-54) | 16 | 0 | A3-PIER4 | 2/A09.25 (plan A02.01) | [DERIVED]
TYPE CANOPY-COL
CANOPY-COL #A3-CW1 - Drive-up canopy column wrap at grid 1 / F (bubble 5/A09.25) | A3-CW1 | 5.668 | 10.5 | 0 | 3-5/8" | 16 | 0 | Drive-up canopy column wrap at grid 1 / F (bubble 5/A09.25) | 5/A09.25 | [DERIVED]
CANOPY-COL #A3-CW2 - Drive-up canopy column wrap at grid 1 / E.4 (bubble 5/A09.25) | A3-CW2 | 5.668 | 10.5 | 0 | 3-5/8" | 16 | 0 | Drive-up canopy column wrap at grid 1 / E.4 (bubble 5/A09.25) | 5/A09.25 | [DERIVED]
CANOPY-COL #A3-CW3 - Drive-up canopy column wrap at grid 1 / C.5 (bubble 5/A09.25) | A3-CW3 | 5.668 | 10.5 | 0 | 3-5/8" | 16 | 0 | Drive-up canopy column wrap at grid 1 / C.5 (bubble 5/A09.25) | 5/A09.25 | [DERIVED]
CANOPY-COL #A3-CW4 - Drive-up canopy column wrap at grid 1 / B.2 (bubble 5/A09.25) | A3-CW4 | 5.668 | 10.5 | 0 | 3-5/8" | 16 | 0 | Drive-up canopy column wrap at grid 1 / B.2 (bubble 5/A09.25) | 5/A09.25 | [DERIVED]
TYPE EXT-PARAPET
EXT-PARAPET #A3-P-G - Tower (HP) parapet on grid G from grid 2 to grid 4 over Vestibule 100 entrance | A3-P-G | 16.82 | 4.292 | 0 | 6" (600S162-54 parapet infill, 11/S5.10) | 16 | 0 | Tower (HP) parapet on grid G from grid 2 to grid 4 over Vestibule 100 entrance | 4/A09.26; 11/S5.10 | [DERIVED]
EXT-PARAPET #A3-P-4R - Tower (HP) east return stub on grid 4, from grid G parapet inner face south past grid F (free end) | A3-P-4R | 3.678 | 4.292 | 0 | 6" (600S162-54 parapet infill, 11/S5.10) | 16 | 0 | Tower (HP) east return stub on grid 4, from grid G parapet inner face south past grid F (free end) | 4/A09.26; 11/S5.10; 1/A02.02 | [DERIVED]
EXT-PARAPET #A3-P-F - Main (LP) north parapet on grid F from grid 4 to grid 8 | A3-P-F | 39.873 | 2.042 | 0 | 6" (600S162-54 parapet infill, 11/S5.10) | 16 | 0 | Main (LP) north parapet on grid F from grid 4 to grid 8 | 4/A09.26; 11/S5.10 | [DERIVED]
EXT-PARAPET #A3-P-8a+A3-P-8b - East (LP) parapet on grid 8 from grid F to grid B (HI roof) + East (LP) parapet on grid 8 from grid B to grid A (LOW roof) | A3-P-8a+A3-P-8b | 75.44 | 2.981 | 0 | 6" (600S162-54 parapet infill, 11/S5.10) | 16 | 0 | East (LP) parapet on grid 8 from grid F to grid B (HI roof) + East (LP) parapet on grid 8 from grid B to grid A (LOW roof) | 4/A09.26; 11/S5.10 | [DERIVED]
EXT-PARAPET #A3-P-A - South (LP) parapet on grid A from grid 3 to grid 8 | A3-P-A | 52.833 | 4.885 | 0 | 6" (600S162-54 parapet infill, 11/S5.10) | 16 | 0 | South (LP) parapet on grid A from grid 3 to grid 8 | 4/A09.26; 11/S5.10 | [DERIVED]
EXT-PARAPET #A3-P-3a+A3-P-3b - West (LP) parapet on grid 3 from grid D to grid B (HI roof) + West (LP) parapet on grid 3 from grid B to grid A (LOW roof) | A3-P-3a+A3-P-3b | 47.427 | 3.535 | 0 | 6" (600S162-54 parapet infill, 11/S5.10) | 16 | 0 | West (LP) parapet on grid 3 from grid D to grid B (HI roof) + West (LP) parapet on grid 3 from grid B to grid A (LOW roof) | 4/A09.26; 11/S5.10 | [DERIVED]
EXT-PARAPET #A3-P-D - Jog (HP) parapet on grid D from grid 2 to grid 3 over the ATM Room 102 south wall | A3-P-D | 3.86 | 4.292 | 0 | 6" (600S162-54 parapet infill, 11/S5.10) | 16 | 0 | Jog (HP) parapet on grid D from grid 2 to grid 3 over the ATM Room 102 south wall | 4/A09.26; 11/S5.10 | [DERIVED]
EXT-PARAPET #A3-P-2 - West tower (HP) parapet on grid 2 from grid G to grid D | A3-P-2 | 29.007 | 4.292 | 0 | 6" (600S162-54 parapet infill, 11/S5.10) | 16 | 0 | West tower (HP) parapet on grid 2 from grid G to grid D | 4/A09.26; 11/S5.10 | [DERIVED]
| TOTAL - PARTITIONS | 965.069 |  |  |  |  | 15822.36
TYPE OTHER FRAMING (NOT A PARTITION)
storefront_cripples #A3-SFC-G - North (grid G) vestibule entrance storefront head, between piers at grid 2 and grid 4 | A3-SFC-G | 12.562 | 4.983 | 1 | 6" | 16 | 86.36 | North (grid G) vestibule entrance storefront head, between piers at grid 2 and grid 4 | 2/A09.26 | [DERIVED]
storefront_cripples #A3-SFC-F - North (grid F) storefront head from pier at grid 4 to N1 (Central Zone 103 / Waiting 104) | A3-SFC-F | 26.25 | 4.525 | 1 | 6" | 16 | 180.47 | North (grid F) storefront head from pier at grid 4 to N1 (Central Zone 103 / Waiting 104) | 2/A09.26 | [DERIVED]
storefront_cripples #A3-SFC-W - West (grid 2) storefront head between pier at G/F and W1 (Vestibule 100) | A3-SFC-W | 6.5 | 4.692 | 1 | 6" | 16 | 44.69 | West (grid 2) storefront head between pier at G/F and W1 (Vestibule 100) | 2/A09.26 | [DERIVED]
fascia_box #A3-FB-N - North canopy fascia, full north edge (drive-up canopy NW corner to east side canopy NE corner) | A3-FB-N | 78.167 | 1.979 | 0 | 3-5/8" | 16 | 0 | North canopy fascia, full north edge (drive-up canopy NW corner to east side canopy NE corner) | 3/A09.26 | [DERIVED]
fascia_box #A3-FB-W - Drive-up canopy west fascia (outside grid 1) | A3-FB-W | 55.896 | 1.979 | 0 | 3-5/8" | 16 | 0 | Drive-up canopy west fascia (outside grid 1) | 16/A09.27 | [DERIVED]
fascia_box #A3-FB-S1 - Drive-up canopy south fascia (grid B.2/B, from canopy west edge to grid 3 wall) | A3-FB-S1 | 21.5 | 1.979 | 0 | 3-5/8" | 16 | 0 | Drive-up canopy south fascia (grid B.2/B, from canopy west edge to grid 3 wall) | 16/A09.27 | [DERIVED]
fascia_box #A3-FB-S2 - South door-123 canopy fascia (grid A between grids 3.4 and 5+), front + two end returns | A3-FB-S2 | 29 | 1.979 | 0 | 3-5/8" | 16 | 0 | South door-123 canopy fascia (grid A between grids 3.4 and 5+), front + two end returns | 7/A09.26 (SIM per F/A09.22) | [DERIVED]
fascia_box #A3-FB-E - East side canopy fascia along grid 8 (F to ~B.2) + south end return | A3-FB-E | 56.25 | 1.979 | 0 | 3-5/8" | 16 | 0 | East side canopy fascia along grid 8 (F to ~B.2) + south end return | 7/A09.26 | [DERIVED]
ceiling_transition #A5-T1 - N edge of Waiting 104 GB 11'-0" island against Central Zone 103 ACT-4 11'-6" | A5-T1 | 17.028 | 4.375 | 1 | 3-5/8" | 16 | 17.03 | N edge of Waiting 104 GB 11'-0" island against Central Zone 103 ACT-4 11'-6" | 7/A09.33 | [DERIVED]
ceiling_transition #A5-T2 - W edge of Waiting 104 GB 11'-0" island against Central Zone 103 ACT-4 11'-6" | A5-T2 | 30 | 4.375 | 1 | 3-5/8" | 16 | 30 | W edge of Waiting 104 GB 11'-0" island against Central Zone 103 ACT-4 11'-6" | 7/A09.33 | [DERIVED]
ceiling_transition #A5-T3 - E edge of Waiting 104 GB 11'-0" island against Central Zone 103 ACT-4 11'-6" | A5-T3 | 30 | 4.375 | 1 | 3-5/8" | 16 | 30 | E edge of Waiting 104 GB 11'-0" island against Central Zone 103 ACT-4 11'-6" | 7/A09.33 | [DERIVED]
soffit_side #A5-SS1 - W long side of the CSR soffit (GB 8'-0") in Cash Window 116, N of grid B | A5-SS1 | 6.55 | 7.375 | 1 | 3-5/8" | 16 | 9.82 | W long side of the CSR soffit (GB 8'-0") in Cash Window 116, N of grid B | 10/A09.33 | [DERIVED]
soffit_side #A5-SS2 - W long side of the CSR soffit (GB 8'-0") in Cash Window 116, S of grid B | A5-SS2 | 5.471 | 5.05 | 1 | 3-5/8" | 16 | 8.21 | W long side of the CSR soffit (GB 8'-0") in Cash Window 116, S of grid B | 10/A09.33 | [DERIVED]
soffit_side #A5-SS3 - E long side of the CSR soffit (GB 8'-0") in Cash Window 116, N of grid B | A5-SS3 | 6.55 | 7.375 | 1 | 3-5/8" | 16 | 9.82 | E long side of the CSR soffit (GB 8'-0") in Cash Window 116, N of grid B | 10/A09.33 | [DERIVED]
soffit_side #A5-SS4 - E long side of the CSR soffit (GB 8'-0") in Cash Window 116, S of grid B | A5-SS4 | 5.471 | 5.05 | 1 | 3-5/8" | 16 | 8.21 | E long side of the CSR soffit (GB 8'-0") in Cash Window 116, S of grid B | 10/A09.33 | [DERIVED]
vestibule_head #A4-VH-101 - Vestibule head framing over the all-glass line between Vestibule 100 and 24 HR Vestibule 101 (opening 101) | A4-VH-101 | 15.646 | 5.375 | 0 | 3-5/8" | 16 | 0 | Vestibule head framing over the all-glass line between Vestibule 100 and 24 HR Vestibule 101 (opening 101) | 6/A12.10 | [DERIVED]
vestibule_head #A4-VH-100A - Vestibule head framing over the all-glass line on grid 4 between Vestibule 100 and Central Zone 103 (opening 100A) | A4-VH-100A | 6.417 | 4.383 | 1 | 3-5/8" | 16 | 9.63 | Vestibule head framing over the all-glass line on grid 4 between Vestibule 100 and Central Zone 103 (opening 100A) | 4/A12.10 | [DERIVED]
grille_head #A4-GH-103 - Coiling grille 103 head framing on grid 4 between 24 HR Vestibule 101 and Central Zone 103 | A4-GH-103 | 13.333 | 2 | 2 | 2-1/2" | 16 | 26.67 | Coiling grille 103 head framing on grid 4 between 24 HR Vestibule 101 and Central Zone 103 | 4/A08.21 | [DERIVED]
roof_step #A6-RS-1 - Roof step at grid B, outer row above the low roof (nailbase + membrane, 2X FRT blocking on top) | A6-RS-1 | 51.594 | 3.112 | 0 | 3-5/8" | 16 | 0 | Roof step at grid B, outer row above the low roof (nailbase + membrane, 2X FRT blocking on top) | 4/A02.02 | [DERIVED]
roof_step #A6-RS-2 - Roof step at grid B, row on the high-roof side from the high steel down to the soffit | A6-RS-2 | 51.594 | 3.46 | 1 | 3-5/8" | 16 | 178.52 | Roof step at grid B, row on the high-roof side from the high steel down to the soffit | 4/A02.02 | [DERIVED]
roof_step #A6-RS-3 - Roof step at grid B, row under the low deck down to the soffit | A6-RS-3 | 51.594 | 1.131 | 1 | 3-5/8" | 16 | 58.35 | Roof step at grid B, row under the low deck down to the soffit | 4/A02.02 | [DERIVED]
alcove #A1-10+A1-10S+A1-10N - Untagged drinking-fountain alcove off CORRIDOR 111 (back wall + N and S returns) set into the restroom block between WOMEN'S RESTROOM 114 and MEN'S RESTROOM 113 + drinking-fountain alcove south return (CORRIDOR 111 side of the B2 line), from the alcove back face x 1099.68 to the B2 face x 1123.08 + drinking-fountain alcove north return (CORRIDOR 111 side of the B2 line), from the alcove back face x 1099.68 to the B2 face x 1123.08 | A1-10+A1-10S+A1-10N | 7.487 | 12.192 | 1.8 | 3-5/8" | 16 | 121.38 | Untagged drinking-fountain alcove off CORRIDOR 111 (back wall + N and S returns) set into the restroom block between WOMEN'S RESTROOM 114 and MEN'S RESTROOM 113 + drinking-fountain alcove south return (CORRIDOR 111 side of the B2 line), from the alcove back face x 1099.68 to the B2 face x 1123.08 + drinking-fountain alcove north return (CORRIDOR 111 side of the B2 line), from the alcove back face x 1099.68 to the B2 face x 1123.08 | 3/A12.01 | [DERIVED]
stub #A2-G1-STUB - 4" untagged stub of the W office-front line (G1 thickness) between G wall A2-G-01 and the office 109 first jamb | A2-G1-STUB | 0.333 | 15.375 | 0 | 1-5/8" | 16 | 0 | 4" untagged stub of the W office-front line (G1 thickness) between G wall A2-G-01 and the office 109 first jamb | 5/A12.01 | [DERIVED]

## Material Summary
MATERIAL SUMMARY - NET / WASTE / PURCHASE
Waste lives HERE, in its own column, applied ONCE: Pieces = ROUNDUP(Net x (1 + waste) / stock). Every stock length, coverage and yield is an Inputs cell.
Material | Unit | Net | Waste % | Waste | Purchase | Selling unit | Pieces to buy | Where it comes from | Yield check (live formula)
6" metal stud (LF of material) | LF | 4490.17 | 0.15 | 673.5255 | 5163.6955 | stick 20 ft | 259 | familias_out.json '6" stud (all gauges)'; 1/A09.25
3-5/8" metal stud (LF of material) | LF | 6980.52 | 0.15 | 1047.078 | 8027.598 | stick 20 ft | 402 | familias_out.json '3-5/8" stud (all gauges)'; 6/A12.01
1-5/8" metal stud (LF of material) | LF | 4052.22 | 0.15 | 607.833 | 4660.053 | stick 20 ft | 234 | familias_out.json '1-5/8" stud'
6" parapet infill stud (LF of material) | LF | 1014.52 | 0.15 | 152.178 | 1166.698 | stick 20 ft | 59 | familias_out.json '6" parapet stud'; 4/A09.26
Track, ceilings / soffits / canopy | LF | 1298.75 | 0.15 | 194.8125 | 1493.5625 | run 10 ft | 150 | familias_out.json 'ceiling / soffit track'
Bracing 1-1/2" C.R. channel @ 48" O.C. | LF | 2516.87 | 0.15 | 377.5305 | 2894.4005 | C.R. channel 16 ft | 181 | familias_out.json 'bracing C.R. channel'
Purlin, top track to deck | LF | 246.9 | 0.15 | 37.035 | 283.935 | run 10 ft | 29 | familias_out.json 'purlin (track to deck)'
Header / metal stud box beam | LF | 796.71 | 0.15 | 119.5065 | 916.2165 | stick 20 ft | 46 | familias_out.json 'header / box beam'
Sill track | LF | 119.12 | 0.15 | 17.868 | 136.988 | run 10 ft | 14 | familias_out.json 'sill track'
Furring channel (ceilings) | LF | 779.51 | 0.15 | 116.9265 | 896.4365 | hat channel 12 ft | 75 | familias_out.json 'furring channel'
Carrying channel (ceilings) | LF | 323.56 | 0.15 | 48.534 | 372.094 | C.R. channel 16 ft | 24 | familias_out.json 'carrying channel'
Hanger wire | LF | 530.15 | 0.15 | 79.5225 | 609.6725 | continuous coil (LF) | 610 | familias_out.json 'hanger wire'
5/8" gypsum board, regular | SF | 17364.35 | 0.06 | 1041.861 | 18406.211 | 4x12 ft sheet (Inputs) | 384 | familias_out.json '5/8" gyp board regular (walls + ceilings)'
5/8" gypsum board, MOISTURE RESISTANT | SF | 258.81 | 0.06 | 15.5286 | 274.3386 | 4x12 ft sheet (Inputs) | 6 | familias_out.json '5/8" gyp MOISTURE RESISTANT'
Ballistic panel UL752 | SF | 83.13 | 0.06 | 4.9878 | 88.1178 | 4x8 ft sheet | 3 | familias_out.json 'ballistic panel'
3/8" gypsum board | SF | 63.6 | 0.06 | 3.816 | 67.416 | 4x12 ft sheet (Inputs) | 2 | familias_out.json '3/8" gyp board'
5/8" glass mat sheathing (exterior face of the stud) | SF | 368.75 | 0.06 | 22.125 | 390.875 | 4x8 ft sheet | 13 | familias_out.json '5/8" glass mat sheathing'
5/8" EXTERIOR gypsum sheathing | SF | 961.09 | 0.06 | 57.6654 | 1018.7554 | 4x8 ft sheet | 32 | familias_out.json '5/8" EXTERIOR gyp sheathing'
Blocking FRT / 2X FRT wood | LF | 1002.63 | 0.06 | 60.1578 | 1062.7878 | piece 8 ft | 133 | familias_out.json 'FRT blocking'; 1/A08.01
Stud blocking at edge of gypboard (structural detail) | LF | 574.93 | 0.15 | 86.2395 | 661.1695 | stick 20 ft | 34 | familias_out.json metal_blocking_by_origin 'metal stud blocking (362CR / STUD BLOCKING)' (edge)
Metal stud blocking at wall-mounted items (notes) | LF | 74.39 | 0.15 | 11.1585 | 85.5485 | stick 20 ft | 5 | familias_out.json metal_blocking_by_origin 'metal stud blocking (362CR / STUD BLOCKING)' (items)
METAL trim - corner bead, casing bead, shadow molding, gypsum edge trim | LF | 1041.42 | 0.15 | 156.213 | 1197.633 | trim stick 10 ft | 120 | familias_out.json 'metal trim (corner bead, casing, shadow molding)'; 8/A12.01
Cement board (substrate under the FRP cove base band) | SF | 31.37 | 0.06 | 1.8822 | 33.2522 | 3x5 ft sheet | 3 | familias_out.json 'cement board'; 1/A08.01
FRP panels | SF | 329.74 | 0.06 | 19.7844 | 349.5244 | 4x8 ft sheet | 11 | familias_out.json 'FRP'; D/A08.01
Framed openings - MEP, light slots and diffusers | LF | 928.25 | 0.15 | 139.2375 | 1067.4875 | stick 20 ft | 54 | framed_openings_out.json 'framed openings MEP' (framed_openings.py)
Bottom track 3-5/8" | LF | 249.43 | 0.15 | 37.4145 | 286.8445 | run 10 ft | 29 | familias_out.json track_by_element 'bottom track (all)' (R73.3)
Bottom track 6" | LF | 308.02 | 0.15 | 46.203 | 354.223 | run 10 ft | 36 | familias_out.json track_by_element 'bottom track (all)' (R73.3)
Bottom track 1-5/8" | LF | 293.1 | 0.15 | 43.965 | 337.065 | run 10 ft | 34 | familias_out.json track_by_element 'bottom track (all)' (R73.3)
Bottom track - other framing (not a partition type, see source) | LF | 58.64 | 0.15 | 8.796 | 67.436 | run 10 ft | 7 | familias_out.json track_by_element 'bottom track (all)' (R73.3)
Parapet bottom track | LF | 268.94 | 0.15 | 40.341 | 309.281 | run 10 ft | 31 | familias_out.json track_by_element 'bottom track (all)' (R73.3)
Bottom track - roof step and heads (vestibule / bulkhead) | LF | 176.84 | 0.15 | 26.526 | 203.366 | run 10 ft | 21 | familias_out.json track_by_element 'bottom track (all)' (R73.3)
Top / deflection track 3-5/8" | LF | 249.43 | 0.15 | 37.4145 | 286.8445 | run 10 ft | 29 | familias_out.json track_by_element 'top / deflection track (all)' (R73.3)
Top / deflection track 6" | LF | 308.02 | 0.15 | 46.203 | 354.223 | run 10 ft | 36 | familias_out.json track_by_element 'top / deflection track (all)' (R73.3)
Top / deflection track 1-5/8" | LF | 293.1 | 0.15 | 43.965 | 337.065 | run 10 ft | 34 | familias_out.json track_by_element 'top / deflection track (all)' (R73.3)
Top / deflection track - other framing (not a partition type, see source) | LF | 58.64 | 0.15 | 8.796 | 67.436 | run 10 ft | 7 | familias_out.json track_by_element 'top / deflection track (all)' (R73.3)
Parapet top track | LF | 268.94 | 0.15 | 40.341 | 309.281 | run 10 ft | 31 | familias_out.json track_by_element 'top / deflection track (all)' (R73.3)
Top track - roof step and heads (vestibule / bulkhead) | LF | 176.84 | 0.15 | 26.526 | 203.366 | run 10 ft | 21 | familias_out.json track_by_element 'top / deflection track (all)' (R73.3)
3-5/8" stud, framed soffit 9/A12.08 (LF) | LF | 37.58 | 0.15 | 5.637 | 43.217 | stick 20 ft | 3 | familias_out.json stud_by_element '3-5/8" stud (all gauges)' (v76)
Blocking 2X wood (not labeled FRT) | LF | 4 | 0.06 | 0.24 | 4.24 | piece 8 ft | 1 | familias_out.json wood_blocking_lf 'FRT blocking' (v76)
5/8" FRT plywood sheathing (canopy and soffits) | SF | 2143.09 | 0.06 | 128.5854 | 2271.6754 | 4x12 ft sheet (Inputs) | 48 | familias_out.json FRT plywood by material; canon rows
Exterior sheathing 5/8" FRT plywood bonded to 2-1/2" polyiso | SF | 4015.65 | 0.06 | 240.939 | 4256.589 | 4x12 ft sheet (Inputs) | 89 | familias_out.json FRT plywood by material; canon rows
FRT plywood substrate (3/4 in.) | SF | 344.74 | 0.06 | 20.6844 | 365.4244 | 4x12 ft sheet (Inputs) | 8 | familias_out.json FRT plywood by material; canon rows
3/4" FRT plywood at storefront piers | SF | 23.6 | 0.06 | 1.416 | 25.016 | 4x12 ft sheet (Inputs) | 1 | familias_out.json FRT plywood by material; canon rows
5/8" FRT plywood at canopy column wraps | SF | 238.06 | 0.06 | 14.2836 | 252.3436 | 4x12 ft sheet (Inputs) | 6 | familias_out.json FRT plywood by material; canon rows
FRT plywood substrate (5/8 in.) | SF | 6.03 | 0.06 | 0.3618 | 6.3918 | 4x12 ft sheet (Inputs) | 1 | familias_out.json FRT plywood by material; canon rows
Sealant at base of gypsum (exterior, not acoustical) | LF | 210.88 | 0.06 | 12.6528 | 223.5328 | tube (25 LF per tube) | 9 | familias_out.json sealant_exterior_lf 'base of gypsum (exterior)'
Hanger wire 12 ga - hanger count (one per hanger, height per room) | PCS | 113 | 0 | 0 | 113 |  | 113 | familias_out.json hanger_pcs.total_pcs; wire bought on the LF row
Additional head track at openings over 4'-0" wide | LF | 56 | 0.15 | 8.4 | 64.4 | run 10 ft | 7 | accesorios.py [CRITERION]: HEAD TRACK @ NON LOAD BRG: ADD FULL LENGTH ADDL HEAD TRACK @ OPNG > 4'-0"; Estimator user decision #1: R.O. + 1'-4" (8" bearing each side)
Stud reinforcement at MEP penetrations | PCS | 32 | 0 | 0 | 32 | each | 32 | accesorios.py [CRITERION]: 6/S5.20 '16 GAUGE PLATE' reinforcement at penetrations (structure_info.metal_stud_schedule_7_S5_20.penetrations); M01.01 duct pair crossing both faces of A1-01 at 1489.92/1510.92 pt (mep.cruces, registered); 6/S5.20 '16 GAUGE PLATE' reinfor
Extra framing - ATM recess (only what a detail prints at the recess; the wall stays in its type) | LF | 32.37 | 0.15 | 4.8555 | 37.2255 | stick 20 ft | 2 | accesorios.py [DERIVED]: 6/A08.11; 4/A09.26; C/A09.21 (plan A02.01); 6/A08.11: "2 1/2" METAL STUD SISTERED TO 6" METAL STUD W/ MINERAL WOOL INSULATION"; 6/A08.11: "FIBER CEMENT PANEL ON FURRING ON 5/8" FRT PLYWOOD"
2-1/2" CFMF @ 16" O.C. at coiling grille head (4/A08.21) | LF | 10.43 | 0.15 | 1.5645 | 11.9945 | stick 20 ft | 1 | accesorios.py [DERIVED]: 4/A08.21
Gypsum board jamb return at openings | SF | 67.16 | 0.06 | 4.0296 | 71.1896 | 4x12 ft sheet (Inputs) | 2 | accesorios.py [CRITERION]: Estimator criterion (return width = 6" stud depth, not dimensioned; RFI with delta at 0.20 ft)
PVC trim - edge trim molding and inside corner molding at the FRP | LF | 221.49 | 0.06 | 13.2894 | 234.7794 | trim stick 10 ft | 24 | accesorios.py [DERIVED]: A-D/A08.01 restroom elevations dim string 6" + 5'-0" TO TOP OF FRP (FRP panel 5'-0" above the 6" CT-12C cove base, top at 5'-6" AFF); 3/A08.01 restroom FRP/tile detail; 1/A08.01 vector polygon (rectangle with one step at the corridor-side w
Power-driven fasteners and duct sleeves | PCS | 301 | 0 | 0 | 301 | each | 301 | accesorios.py [DERIVED]: 11/S5.10 'PAFs SPACED AT 12" O.C. MAX.'; M01.01 duct pair crossing both faces of A1-01 at 1489.92/1510.92 pt (mep.cruces, registered); M01.01 duct pair crossing both faces of A1-05 at 1332.96/1347.96 pt (mep.cruces, registered); M01.01 duct
Access panel 2'x2' locking | PCS | 1 | 0 | 0 | 1 | each | 1 | accesorios.py [CONFIRMED]: A04.01 key note 4 '2' X 2' LOCKING ACCESS PANEL. KEYED TO MATCH MAIN ENTRY.' - one access door symbol with key note 4 (only key note 4 circle on the RCP)
Drywall screws 1-1/4" bugle head | PCS | 21224.11 | 0 | 0 | 21224.11 | each | 21225 | accesorios.py [DERIVED]: Inputs!B20 (Drywall screws per SF of board = 1.2) x 17686.8 SF of board | 21224.16
Framing screws, pan head self-drilling | PCS | 7092 | 0 | 0 | 7092 | each | 7092 | accesorios.py [DERIVED]: Inputs!B21 (Framing screws per stud piece = 4) x 1773 stud pieces | 7092
Power-driven fasteners, slab pins for the bottom track | PCS | 546.29 | 0 | 0 | 546.29 | each | 547 | accesorios.py [DERIVED]: 546.29 LF of interior bottom track on slab / Inputs!B22 (Power-driven pin spacing (ft) = 1) | 546.29
Expansion anchors Hilti 1/4" Kwik Bolt II, exterior bottom track @ 8" O.C. | PCS | 321.3 | 0 | 0 | 321.3 | each | 322 | accesorios.py [DERIVED]: 214.21 LF of exterior bottom track on slab / Inputs!B25 (Expansion anchor spacing (ft) = 0.6667) | 321.2989
Joint compound, all purpose | LB | 1273.45 | 0 | 0 | 1273.45 | lb | 1274 | accesorios.py [DERIVED]: Inputs!B23 (Joint compound (lb per SF) = 0.072) x 17686.8 SF of board | 1273.4496
Joint tape, paper | LF | 6544.1 | 0 | 0 | 6544.1 | LF | 6545 | accesorios.py [DERIVED]: Inputs!B24 (Joint tape (LF per SF) = 0.37) x 17686.8 SF of board | 6544.116
Level 5 finish | SF | 859.26 | 0.06 | 51.5556 | 910.8156 | SF | 911 | accesorios.py [DERIVED]: A05.01 key note 12 circle + WC-18 tag in 105; 1/A11.04 OFFICE 1 elevation: WC-18 full wall, 11'-9 1/4" V.I.F.; height A04.01 RCP (p.29): offices 105-110 '9'-0" ACT-4'; A05.01 key note 12 circle + WC-18 tag in 106; 6/A11.01 OFFICE 2 elevatio
Deflection clips at non-load-bearing walls to structure | PCS | 0 | 0 | 0 | 0 | each | 0 | accesorios.py [CRITERION]: S1.11 LIGHT GAUGE STEEL FRAMING note 2 'PROVIDE MANUFACTURER'S STANDARD VERTICAL DEFLECTION CLIPS AT NON-LOAD-BEARING WALLS ... MAX. 1 INCH VERTICAL UPWARD OR DOWNWARD MOVEMENT'; 3/A12.01, 1/A12.01, 4/A12.01, 9/A12.01, 8/A12.01 'CONTINUOUS

## Pending Items
RFI | Question / condition | Delta of each alternative
RFI-ACC-additional-head-track | additional head track: openings with their own box (openings_extra) > 4'-0": do they also take the additional head track of HEAD TRACK @ NON LOAD BRG: ADD FULL LENGTH ADDL HEAD TRACK @ OPNG > 4'-0"? | 100.54 lf
RFI-ACC-stud-reinforcement-mep | stud reinforcement MEP: plates at double-row stud walls: one per cut row (R72.9) vs one per crossing | -7 pcs
RFI-ACC-stud-reinforcement-mep-2 | stud reinforcement MEP: pipes over 1 in. through the stud web: the penetration detail draws a plate (R73.5) | 14 pcs
RFI-ACC-stud-reinforcement-mep-3 | stud reinforcement MEP: duct / fire damper openings listed outside the registered MEP sweep (R73.5) | 4 pcs
RFI-ACC-gypsum-board-jamb-return | gypsum board jamb return: jamb return width not dimensioned | -40.29 sf
RFI-ACC-slab-pins | slab pins: pin spacing: 12" (interior anchorage) vs 16" (fastener schedule) vs 24" (type K box) | 16in: -136.57 pcs; 24in: -273.14 pcs
RFI-ACC-deflection-clips | deflection clips: deflection clips: the general note asks for them at non-load-bearing walls and the partition details draw a slip / deflection track (R73.6) | 540 pcs
RFI-A5-CARRY | RFI-A5-CARRY: direction of carrying channels in suspended GWB ceilings not shown; E-W assumed. Delta of N-S: 100 VESTIBULE: carrying 47.48 LF / 15 hangers (E-W) vs 37.98 LF / 15 hangers (N-S); 101 24 HR VESTIBULE: carrying 54.8 LF / 20 hangers (E-W) vs 47.82 LF / 20 hangers (N-S); 104 WAITING: carrying 153.25 LF / 54 hangers (E-W) vs 180.0 LF / 54 hangers (N-S); 114 WOMEN'S RESTROOM: carrying 34.02 LF / 12 hangers (E-W) vs 25.77 LF / 12 hangers (N-S); 113 MEN'S RESTROOM: carrying 34.0 LF / 12 hangers (E-W) vs 25.76 LF / 12 hangers (N-S) | Delta of N-S: 100 VESTIBULE: carrying 47.48 LF / 15 hangers (E-W) vs 37.98 LF / 15 hangers (N-S); 101 24 HR VESTIBULE: carrying 54.8 LF / 20 hangers (E-W) vs 47.82 LF / 20 hangers (N-S); 104 WAITING: carrying 153.25 LF / 54 hangers (E-W) vs 180.0 LF / 54 hangers (N-S); 114 WOMEN'S RESTROOM: carrying 34.02 LF / 12 hangers (E-W) vs 25.77 LF / 12 hangers (N-S); 113 MEN'S RESTROOM: carrying 34.0 LF / 12 hangers (E-W) vs 25.76 LF / 12 hangers (N-S)
RFI-A5-RR-DIFF | Restrooms 113/114: A04.01 shows two 2'x2' HVAC diffuser/grille symbols per room; M01.01 shows two single-section slot diffusers (TBDI-10, 2'-0") per room. Carried M01.01. Delta if 2'x2' framed: 4 x 2 x (2+2) = 32 LF vs slots 4 x 2 x 2.294 = 18.35 LF sides (+ends PENDING). | Delta if 2'x2' framed: 4 x 2 x (2+2) = 32 LF vs slots 4 x 2 x 2.294 = 18.35 LF sides (+ends PENDING).
RFI-A5-VS | Vertical studs of 7/A09.33 transitions: spacing not printed; 16" O.C. carried (8/A09.33). Delta @24": Waiting transitions 77.03 LF. | Delta @24": Waiting transitions 77.03 LF.
RFI-A5-CSR | 10/A09.33 draws a scheduled partition on one side of the CSR soffit; 4/A12.08 shows ACT-4 9'-0" on both sides. Carried 2 drop lines (soffit_side both sides). Delta if one side is a partition: -2 soffit_side segments on that side (12.02 LF track x2, studs). | Delta if one side is a partition: -2 soffit_side segments on that side (12.02 LF track x2, studs).
RFI-ASM-SLOPE-59-13 | Sloped low zone grid B -> A (S2.20 13'-0 5/8" -> 12'-6 3/8", SLOPE): stud and board heights are carried at each wall's own high end (rule 59.13, interpolated). The older SKILL deck-height prose (zone high end for every wall) gives the alternative below; contradiction filed for the arbiter (morning-review folder). | if every low-zone wall is cut at the zone high end 13.0521: + dH ft per stud and per SF of board to deck: A1-05 +0.087, A1-06 +0.131, A1-07 +0.091, A1-08 +0.091, A1-09 +0.284, A1-10 +0.097, A1-10S +0.193, A1-10N +0.101, A1-12 +0.132, A1-13 +0.12, A1-14b +0.002, A1-16b +0.002, A1-17 +0.136, A2-B-01 +0.227, A2-B-02 +0.307, A2-B-03 +0.311, A2-B-04 +0.388, A2-B-05 +0.356, A2-B-06 +0.231, A2-B2-02b +0.002, A2-B2-03 +0.189, A2-B2-04 +0.279, A2-C1-06 +0.131, A2-C1-07 +0.162, A2-C1-08 +0.132, A2-C1-08E +0.124, A3-E1b +0.002, A3-W2b +0.002, A3-P-8b +0.002, A3-P-3b +0.002, A5-SS2 +0.002, A5-SS4 +0.002
RFI-ASM-BEAM-A2-B-02 | A2-B-02: vigas_sobre_walls.py puts S2.20 W8X10 (axis 1509.85 pt) over 5.287 ft of the 11.719 ft wall (45.1 %); the record stops under the beam (E26 / R72.4). Confirm whether the studs outside the beam (6.432 ft) run to the deck. | +0.657 ft per stud on the 6.432 ft outside the beam (@ 16" O.C., x 1 row(s)) and +0.657 ft x that length per board face to deck
RFI-ASM-BEAM-A2-B-04 | A2-B-04: vigas_sobre_walls.py finds an S2.20 beam line (axis 1586.43 pt) over 5.287 ft of the wall (45.1 %) with no W mark next to it (tool note: no W mark beside the beam, RFI with depth d): depth unknown, studs carried to deck. Confirm the member and whether the studs stop under it. | -d (beam depth, ft) per stud on the 5.287 ft under the beam (@ 16" O.C.) and -d x 5.287 ft per board face to deck
RFI-ASM-BEAM-A2-G-01 | A2-G-01: vigas_sobre_walls.py finds two parallel beams with different marks over the wall (W12X19 3.015 ft, W12X19 3.015 ft, W8X10 3.82 ft); the canon keeps studs to deck; confirm which member the studs stop under (S2.20). | per stud: height difference between the candidate beam depths (W12X19 1.017 ft, W8X10 0.657 ft)
RFI-ASM-BEAM-A2-G-02 | A2-G-02: vigas_sobre_walls.py puts S2.20 W8X10 (axis 1040.57 pt) over 3.36 ft of the 11.625 ft wall (28.9 %); the record stops under the beam (E26 / R72.4). Confirm whether the studs outside the beam (8.265 ft) run to the deck. | +0.657 ft per stud on the 8.265 ft outside the beam (@ 16" O.C., x 2 row(s)) and +0.657 ft x that length per board face to deck
RFI-ASM-BEAM-A2-G-05 | A2-G-05: vigas_sobre_walls.py puts S2.20 W14X30 (axis 1632.8 pt) over 1.795 ft of the 3.253 ft wall (55.2 %); the record stops under the beam (E26 / R72.4). Confirm whether the studs outside the beam (1.458 ft) run to the deck. | +1.15 ft per stud on the 1.458 ft outside the beam (@ 16" O.C., x 2 row(s)) and +1.15 ft x that length per board face to deck
RFI-ASM-BEAM-A2-G1-01 | A2-G1-01: vigas_sobre_walls.py puts S2.20 W8X10 (axis 533.05 pt) over 3.354 ft of the 11.771 ft wall (28.5 %); the record stops under the beam (E26 / R72.4). Confirm whether the studs outside the beam (8.417 ft) run to the deck. | +0.657 ft per stud on the 8.417 ft outside the beam (@ 16" O.C., x 2 row(s)) and +0.657 ft x that length per board face to deck
RFI-ASM-BEAM-A3-W1 | A3-W1: vigas_sobre_walls.py finds two parallel beams with different marks over the wall (W16X26 14.889 ft, W12X19 4.607 ft, W16X26 14.889 ft, W12X19 4.607 ft, W16X26 14.889 ft); the canon keeps stops_under_beam W12X19 (reading A); confirm which member the studs stop under (S2.20). | per stud: height difference between the candidate beam depths (W12X19 1.017 ft, W16X26 1.308 ft)
RFI-ASM-BEAM-A3-SFC-F | A3-SFC-F: vigas_sobre_walls.py finds two parallel beams with different marks over the wall (W16X26 26.242 ft, W16X26 26.242 ft, W18X35 26.242 ft, W16X26 26.242 ft); the canon keeps stops_under_beam W18X35 (reading A); confirm which member the studs stop under (S2.20). | per stud: height difference between the candidate beam depths (W16X26 1.308 ft, W18X35 1.475 ft)
RFI-ASM-K-CORNER | A02.01: the B2K Kevlar hatch of A2-B2K-01 is drawn to x 1655.40, 1.44 pt past the start face of A1-11 (x 1653.96, W tick of the printed 3'-5"). Take-off gives the corner to A1-11 (one owner, R70.2) and adds the jog y 1118.04-1120.68 at x 1653.96 (R76.3). Confirm the Kevlar panel is continuous around the step. | -0.08 ft x panel height per layer on A2-B2K-01: 3/8" ballistic panel -0.08 x 8.0 = -0.64 SF per layer; 5/8" board -0.08 x 15.375 = -1.23 SF per face per layer (jog adds back its own band, ballistic_jogs)
RFI-ASM-MEP-P | Plumbing sheets P01.01 / P01.02 / P02.01 and M01.02 / M02.01 do not register against A02.01 with >= 25 wall-segment votes (mep.py): their pipe / duct crossings of stud walls are not counted geometrically; confirm pipes > 1" through stud webs (6/S5.20 plate each). | +1 plate per stud cut per pipe > 1" crossing a stud wall (count not available without registration)
RFI-ADV-TA | A08.01 legend: TA-2 / TA-13 / TA-14 are recessed but their rough-opening widths are not printed. 0 carried (R71.6). Provide the R.O. of each (spec Div 10). | TA-13 x2 (vector 17.16" > stud bay 14 3/8"): +5.53 LF header (single track) and +5.53 LF sill track; TA-2 (13.0") and TA-14 (14.08") fit the bay: 0
RFI-ADV-MW08 | MW08 blocking: 3/A12.04 (called on 10/A12.04 at the microwave niche) reads PRESSURE TREATED and draws 2 rows; sheet note D (A12.03-A12.06) reads FRTW. Carried FRT x 2 rows over the 7'-7" counter. Confirm material and whether the second row runs the full counter or only the 2'-5" niche. | material: 15.17 LF FRT -> pressure-treated wood (no LF change); rows: if the second row is only at the niche, -5.17 LF (7.583 - 2.417)
RFI-ADV-PF06 | PF-06 wall-hung bi-level fountain (P00.01, no carrier): A02.01 note C requires blocking, no material printed. Carried 3.13 LF metal stud blocking (58.6). | material only: 3.13 LF metal -> FRT (same LF)
RFI-ADV-HATCH | Roof hatch (A02.02 key note 8, 1/A09.30): size not printed; drawn outline 2.833 x 3.433 ft used for the 2x FRT curb blocking (2 plies). Confirm the hatch model / curb size. | per inch of hatch size: +2 x 2 plies x 1/12 ft = +0.333 LF FRT blocking per inch on each side dimension
RFI-ADV-WC20 | WC-20 (A05.01 key note 9, 24 HR Vestibule 101): not in the A00.40 finish legend; extent taken from the leaders at both ends of the diagonal ATM wall, height to the GB 10'-0" ceiling (53.3). Confirm extent and height. | per ft of height: -15.208 SF Level 5 per ft below the ceiling (e.g. to 8'-0": -30.416 SF)
RFI-ADV-A0031 | A05.01 notes A/B and A03.01 note D refer to the FINISH SCHEDULE A00.31; A00.31 is not in the bid set nor in the A00.00 index. It may change the extents of FRP, Level 5 and wallcoverings. | not quantifiable until A00.31 is issued
RFI-ADV-A0812 | A00.60 site note 13 'DRIVE UP ATM. SEE A03.01 & A08.12': A08.12 does not exist in the set (probably A08.11). Confirm. | none if A08.11 is the intended sheet (drive-up ATM already from 5/A08.11 and 6/A08.11)
RFI-ADV-DU-BAND | Drive-up canopy band (W, W-HP, S-HP; 15/A09.27): a dashed sheathing line is drawn on the stud face behind the canopy but not labelled (the 3/A09.26 band labels 5/8" GLASS-MAT SHEATHING). Carried none (R78.13). Confirm. | +112.3 SF 5/8" glass mat if sheathed (56.751 LF x 1.979)
RFI-ADV-GM-BAND | Canopy glass-mat band height: 3/A09.26 nailbase hatch stops at y 501.5 and resumes at y 643.2 = 1.31 ft on the wall (scale checked on the 6" dim); the canon keeps the estimator formula E25 T/STUD - B/STUD = 1.979 ft (fascia elevations). | if the wall geometry is used: glass mat -86.2 SF (129.03 LF x 0.668), nailbase +124.1 SF (185.8 LF x 0.668)
RFI-ADV-CAN-HANGERS | Canopy soffit vertical members: 3/A09.26 (and 7/A09.26) draw two 3 5/8" dashed verticals (~0.86 ft) from the canopy steel to the soffit joist; spacing not printed. Not carried. | about +84 LF 3 5/8" CFMF on the N canopy (one pair per joist: (15 + 34) x 2 x 0.86); E/S/W in proportion
RFI-ADV-RS1-FACE | 4/A02.02: an unlabelled gypsum-hatched layer is drawn on the inner (high-roof) face of RS-1 from the blocking down to the high deck (~1.0 ft). Not carried (no label). | about +52 SF 5/8" exterior gypsum sheathing (51.594 x 1.0)
RFI-ADV-4R-FACE | Tower return 4R: the east face south of F (~2.7 ft) also faces the roof; only one roof-side face is carried. | about +11.5 SF exterior gypsum or about +6 SF nailbase
RFI-ADV-CAN-SHEATH | Canopy soffit sheathing: 4/A09.33 and 5/A09.33 say '5/8" EXTERIOR SHEATHING' while 3/A09.26, 7/A09.26, 16/A09.27 say '5/8" EXT. GRADE FRT PLYWOOD'. Carried plywood. | material only (no SF change)
RFI-ADV-RS-BEAD | Roof step bottom closure (4/A02.02): corner bead at the two open bottom edges not labelled. Not carried. | +103.2 LF corner bead (2 x 51.594) if required
RFI-ADV-G1-STUB | A2-G1-STUB (R74.2 stub, 4" faces) carries no board faces: it may be concealed by the vendor front jamb. | about +20.5 SF 5/8" board (two 4" faces x 2 layers x 15.375)
RFI-ADV-A101-BEHIND-C1 | A1-01 face A (Waiting 104) behind the C1 monitor box A2-C1-05 (10'-0" x 8"): the A1 board behind the box is carried as well as the C1 face (correct by type, concealed). | about -115 SF 5/8" board if the concealed A1 face behind the box is omitted
RFI-ADV-SHELF-ROWS | 11/A12.04 SECTION @ SHELVING OVERHEAD draws 2 blocking pieces per unit; the canon carries one row per mounting level for MW12 / MW05 / MW06A / MW13. | MW12 +7.0 LF; MW05 +3.5, MW06A +6.92, MW13 +11.67 LF FRT if 2 rows each
RFI-ADV-HAT | A09.31: 7/8" hat channel @ 16" O.C. behind the EPS-5 formed metal panel and the composite metal panel: not counted, not excluded. Proposed as panel subcontractor subframing (Div 07) in Clarifications. | not quantified (Div 07 subframing)
RFI-ADV-SIGNAGE | A08.01 KN3 restroom signage 'installed by GC' and A02.01 KN12 wellness signage: no blocking counted (adhesive mount assumed). | +1.333 LF metal blocking per sign if mechanically fastened
RFI-ADV-MW13-CITE | A7-B-MW13 op quotes 'PRESSURE TREATED' (text of 3/A12.04); A12.06 says 'PROVIDE ADDITIONAL BLOCKING' with no material. Citation to be reviewed; material stays FRT per sheet note D. | none (citation only)
A4-RFI-ATM-DU-RO | A4-RFI-ATM-DU-RO: DU ATM R.O. width 2'-2 1/2" (7/A08.11) vs 2'-2 1/8" (26.4") (5/A08.11). Delta header + sill track = 3/8" x (4 box pieces + 1 sill) = 0.16 LF | Delta header + sill track = 3/8" x (4 box pieces + 1 sill) = 0.16 LF
A4-RFI-ATM-DU-OC | A4-RFI-ATM-DU-OC: O.C. of the 2 1/2" sistered studs and of the furring at the DU ATM recess not printed (6/A08.11); 16" O.C. carried. Delta at 24" O.C.: sistered 2 x 6.0 = 12.0 (-6.0 LF); furring 3 x 2.87 = 8.62 (-5.75 LF) | Delta at 24" O.C
A4-RFI-CSR-HDR | A4-RFI-CSR-HDR: header over the 12'-0 1/4" CSR line R.O. (Cash Window 116) not shown; 7/S5.20 tops at 8'-0". If a metal stud box beam (4 pieces): (12.0208 + 1.3333) x 4 = 53.42 LF of header | +53.42 LF header if a 4-piece metal stud box beam is required (not carried)
A4-RFI-VEST-BOX | A4-RFI-VEST-BOX: 'BOX HEADER AS NEEDED' (4-7/A12.10) size / members not printed (E11). Counted as 4 pieces x (R.O. + 1'-4"); confirm member size | n/a: member size only (piece count and LF carried: 4 pieces x (R.O. + 1'-4"))
A4-RFI-103-SCHED | A4-RFI-103-SCHED: A00.30 row 103 HEIGHT 13'-6 1/2" vs grille R.O. 13'-4" wide / ~10'-0" high (A02.01, A08.21); no LF delta in header (width from A02.01) | 0 LF: header width taken from A02.01; schedule height conflict only
A4-RFI-FEC1 | A4-RFI-FEC1: FEC-1 recessed cabinet size not printed (A00.40 size '-', spec 10 44 00). 0 carried; delta if R.O. > stud bay 14 3/8": header + sill (R.O. + 1'-4") x 2 per cabinet | + (R.O. + 1'-4") x 2 LF per cabinet if R.O. > stud bay; 0 carried
A4-RFI-TA | A08.01 TOILET ACCESSORY LEGENDS designate TA-2 RECESSED PAPER TOWEL DISPENSER, TA-13 HAND DRYER W/ ADA COMPLIANT RECESS KIT and TA-14 RECESSED WASTE RECEPTACLE (rows above, width not printed -> 0 + RFI-ADV-TA, R71.6); the other TA items carry no recessed designation | n/a: recessed accessory sizes per cutsheet; framed openings carried per sweep
A4-RFI-SUBSTRATE-WIDTH | A4-RFI-SUBSTRATE-WIDTH: constants.opening_substrate_width_ft (strip width of the 3/4" FRT plywood at heads / jambs of windows, storefronts and door 123) not dimensioned in 11/A09.27, 2/A09.26, 14/A09.27, 3/A09.25, 4/A09.25 -> estimator criterion | n/a: strip width is an estimator criterion; SF of 3/4" FRT plywood substrate scales with the width
RFI-A3-HP-BACK | HP parapet block (T.O. PARAPET 2 20'-0") back faces: A09.02 south/east elevations show key note 7 'EXTERIOR PROTECTION BOARD' on the back of the block over grids 2-4 / D-F, but A02.02 roof plan draws no parapet on grid 4 (D->F) nor grid D (3->4). Not quantified; delta ~ (3.9 + 27) ft x 4.29 ft parapet. | +(3.9 + 27) ft x 4.29 ft of parapet back face if the HP block back faces exist (not carried)
RFI-A3-CANOPY-BEAM | Canopy beams (W16x26/W12x19 CANOPY, HSS10x3 CANOPY) inside the exterior stud cavity (C/A09.21, H/A09.23, 15/A09.27): walls kept continuous to the HI/LOW roof beam (R80.2); split = +track, -stud. | split = +1 track line per beam run, -stud length above the beam (R80.2)
RFI-A3-CANOPY-JOIST | Drive-up canopy soffit 3 5/8" joists spanning up to 21'-6" (16/A09.27) - support / direction RFI. | n/a: support / direction only; joist LF carried per 16/A09.27
RFI-A3-PIER-STUDS | Storefront pier studs_drawn (1/A09.25, 2/A09.25) counted visually - verify. | n/a: studs drawn in 1/A09.25 and 2/A09.25 counted from the drawing
RFI-FO-R-11C-1 | RFI R-11C: opening width not printed (E00.01 light fixture schedule (R-11C description / catalog FSM2L-...-TF-XF2 give no opening width)); Provide opening width for the recessed linear gyp slot (cutsheet); framing ends not carried; ends not carried | +2 x W x 2 LF (ends; W pending)
RFI-FO-R-11C-2 | RFI R-11C: schedule description 12.0 ft vs catalog 20.0 ft; carried 12.0 ft (desc = drawn); alternate 20.0 ft | +32 LF
RFI-FO-R-11CE-3 | RFI R-11CE: opening width not printed (E00.01 light fixture schedule (R-11CE 'SAME AS ABOVE' - no opening width)); Provide opening width for the recessed linear gyp slot (cutsheet); framing ends not carried; ends not carried | +2 x W x 2 LF (ends; W pending)
RFI-FO-R-11CE-4 | RFI R-11CE: schedule description 12.0 ft vs catalog 20.0 ft; carried 12.0 ft (desc = drawn); alternate 20.0 ft | +32 LF
RFI-FO-R-11A-5 | RFI R-11A: opening width not printed (E00.01 schedule R-11A gives no width; 6/A09.33 trimless detail (bubbled in 10/A09.33) prints no opening width); Provide opening width for the recessed linear gyp slot (cutsheet); framing ends not carried; ends not carried | +2 x W x 2 LF (ends; W pending)
RFI-FO-SD-3SEC-6 | RFI SD-3SEC: opening width not printed (M00.03 schedule 'SD/SDR TITUS TBDI-10 ... (2) 1" SLOTS', size 'SEE DRAWING' - opening width not printed (drawn outer ~7.7")); Provide slot diffuser TBDI-10 2-slot frame width for the GWB opening; ends not carried; ends not carried | +2 x W x 4 LF (ends; W pending)
RFI-FO-SD-1SEC-7 | RFI SD-1SEC: opening width not printed (M00.03 'SD/SDR TITUS TBDI-10 (2) 1" SLOTS', size 'SEE DRAWING' - width not printed); Provide TBDI-10 frame width; A04.01 shows 2'x2' diffuser symbols in the restrooms instead of slots - confirm device; ends not carried | +2 x W x 4 LF (ends; W pending)
RFI-FO-UU1-8 | RFI UU1: opening width not printed (5/A09.33 + 4/A09.33 'CANOPY LINEAR LIGHT DETAIL - TRANS': width 'COORD. W/ FIXTURE CUTSHEET' (not printed); E00.01 catalog LSR-WET-2.5 is a model code, not an opening width); Provide the recess width of the Coronet LSR-WET UU1 (20.0' fixture) in the 5/8" exterior sheathing on 3 5/8" CFMF canopy soffit (4/A09.33 'COORD. W/ FIXTURE CUTSHEET'); framing ends not carried; ends not carried | +2 x W x 1 LF (ends; W pending)
RFI-FO-UU2-9 | RFI UU2: opening width not printed (5/A09.33 + 4/A09.33 'CANOPY LINEAR LIGHT DETAIL - TRANS': width 'COORD. W/ FIXTURE CUTSHEET' (not printed); E00.01 catalog LSR-WET-2.5 is a model code, not an opening width); Provide the recess width of the Coronet LSR-WET UU2 (2.0' fixture) in the 5/8" exterior sheathing on 3 5/8" CFMF canopy soffit (4/A09.33 'COORD. W/ FIXTURE CUTSHEET'); framing ends not carried; ends not carried | +2 x W x 5 LF (ends; W pending)
RFI-FO-UU3-10 | RFI UU3: opening width not printed (5/A09.33 + 4/A09.33 'CANOPY LINEAR LIGHT DETAIL - TRANS': width 'COORD. W/ FIXTURE CUTSHEET' (not printed); E00.01 catalog LSR-WET-2.5 is a model code, not an opening width); Provide the recess width of the Coronet LSR-WET UU3 (3.0' fixture) in the 5/8" exterior sheathing on 3 5/8" CFMF canopy soffit (4/A09.33 'COORD. W/ FIXTURE CUTSHEET'); framing ends not carried; ends not carried | +2 x W x 9 LF (ends; W pending)
RFI-FO-UU4-11 | RFI UU4: opening width not printed (5/A09.33 + 4/A09.33 'CANOPY LINEAR LIGHT DETAIL - TRANS': width 'COORD. W/ FIXTURE CUTSHEET' (not printed); E00.01 catalog LSR-WET-2.5 is a model code, not an opening width); Provide the recess width of the Coronet LSR-WET UU4 (55.0' fixture) in the 5/8" exterior sheathing on 3 5/8" CFMF canopy soffit (4/A09.33 'COORD. W/ FIXTURE CUTSHEET'); framing ends not carried; ends not carried | +2 x W x 4 LF (ends; W pending)
RFI-FO-UU5-12 | RFI UU5: opening width not printed (5/A09.33 + 4/A09.33 'CANOPY LINEAR LIGHT DETAIL - TRANS': width 'COORD. W/ FIXTURE CUTSHEET' (not printed); E00.01 catalog LSR-WET-2.5 is a model code, not an opening width); Provide the recess width of the Coronet LSR-WET UU5 (50.0' fixture) in the 5/8" exterior sheathing on 3 5/8" CFMF canopy soffit (4/A09.33 'COORD. W/ FIXTURE CUTSHEET'); framing ends not carried; ends not carried | +2 x W x 1 LF (ends; W pending)
RFI-FO-UU6-13 | RFI UU6: opening width not printed (5/A09.33 + 4/A09.33 'CANOPY LINEAR LIGHT DETAIL - TRANS': width 'COORD. W/ FIXTURE CUTSHEET' (not printed); E00.01 catalog LSR-WET-2.5 is a model code, not an opening width); Provide the recess width of the Coronet LSR-WET UU6 (16.0' fixture) in the 5/8" exterior sheathing on 3 5/8" CFMF canopy soffit (4/A09.33 'COORD. W/ FIXTURE CUTSHEET'); framing ends not carried; ends not carried | +2 x W x 1 LF (ends; W pending)
RFI-CR-BRACING | RFI bracing: 123.04 LF of C.R. channel bracing runs across openings without studs (53.4, literal). | -123.04 LF of C.R. channel if not run across openings
RFI-CR-DOORS | RFI bottom track: 50.5 LF of door R.O. are NOT deducted from the bottom track (corridas.py). | -50.5 LF of bottom track if door R.O. are deducted
RFI-TYPE-B2K | B2K is tagged on A02.01 (PC0011) but has no row in the A12.01 schedule: carried as B2 + Kevlar per 4/A12.01 [DERIVED], declare in Clarifications | n/a: carried as B2 + Kevlar per 4/A12.01; any other build-up changes the B2K row only
RFI-TYPE-G-GAUGE | G / G1 types: 1-5/8" stud designation / gauge not scheduled | n/a: gauge only (LF unchanged)
RFI-L5-WC20 | RFI-ADV-WC20: WC-20 height / extent not printed | n/a: Level 5 SF changes with the WC-20 extent (L x (10'-0" - base) on that face)
RFI-PLY-2 | 1/A09.25: two hatched 3/4" plies drawn at the jamb but the label is singular '3/4" FRT PLYWOOD': 1 ply carried (label); second ply delta +12.903 SF | delta +12.903 SF
RFI-PLY-3 | 2/A09.25: two hatched 3/4" plies drawn at the jamb but the label is singular '3/4" FRT PLYWOOD': 1 ply carried (label); second ply delta +6.452 SF | delta +6.452 SF
RFI-PLY-4 | 2/A09.25: two hatched 3/4" plies drawn at the jamb but the label is singular '3/4" FRT PLYWOOD': 1 ply carried (label); second ply delta +4.25 SF | delta +4.25 SF
RFI-TRIM-3 | Grille-side bottom corner assumed beaded (TYP.); delta -13.333 LF if only the room side is exposed. | delta -13.333 LF if only the room side is exposed
RFI-BLK-NOTE-C | Blocking at wall-mounted items per general note C (23 items): note C gives no material; metal 362CR stud blocking carried (58.6) | 0 LF: material swap only (the same LF moves from metal stud blocking to the FRT blocking row)
RFI-BLK-30 | A7-B-MW08: RFI-ADV-MW08: 3/A12.04 says 'PROVIDE ADDITIONAL PRESSURE TREATED BLOCKING IN PARTITION' while sheet note D says FRTW; carried FRT (sheet note label). 3/A12.04 is cut at the microwave niche (2'-5" HOLD). | n/a: one row length per item; LF changes with the printed length
RFI-BLK-36 | A7-B-WS: Wall stop blocking material and length not printed: metal 362CR stud blocking one bay per stop assumed; delta to FRT 2x = same LF in the FRT family. | delta to FRT 2x = same LF in the FRT family.
RFI-BLK-54 | A7-B-LOCKERS: Locker width differs between 5/A11.02 (3.75 ft) and the dashed plan footprint (~4.9 ft); rows and material not printed (metal assumed). Delta +1.15 LF. | Delta +1.15 LF
RFI-BLK-61 | A7-B-LADDER: Bracket count follows the 3 levels drawn (the elevation has a break line); blocking length per level = printed ladder width min. 1'-6". | n/a: one row length per item; LF changes with the printed length
RFI-BLK-62 | A7-B-WH1: NTS detail: length per row not printed (one stud bay assumed); 2X without FRT label = wood (R76.7). | n/a: one row length per item; LF changes with the printed length
RFI-BLK-70 | A7-B-GRILLE: Second jamb assumed mirrored (detail 3 'TYP'); height measured in vector (no printed height). | n/a: one row length per item; LF changes with the printed length
RFI-BLK-74 | A6-B-HATCH: RFI-ADV-HATCH: hatch size not printed (drawn outline measured). | n/a: one row length per item; LF changes with the printed length
RFI-SHEET-LEN | 56.8: blocking location not given; carried at the horizontal board joint of faces taller than 12 ft; alternative (a) exterior walls + double-layer types | n/a: blocking LF moves to the alternative location (exterior walls + double-layer types)

## Review Items
121 questions in total, asked ONE at a time in this order: floor plan (partition types A-Z), then the details the floor plan calls, in order
# | Phase | Type / order | Item | Sheet + detail | Image
1/121 | Floor plan | A1 | Double-reading item 1 (Sheet A02.01 (p.24)): LF differs -0.61 LF (20.0 %): A A1-03 3.03 LF vs B B1-03 2.43 LF [matched by position]. Resolution: #1 A1 (A A1-03 / B B1-03) → **B** → A1-03 2.427 LF [R78.35 / R70.2] → A02.01 (p.24) vector layer fills; 6/A12.03 MW01 sections (SCHED. PARTITION) → /home/user/boa29b/work/etapas/3_revision/res_img/R001.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R001.png
2/121 | Floor plan | A1 | Double-reading item 2 (Sheet A02.01 (p.24)): LF differs -1.19 LF (13.7 %): A A1-10 8.68 LF vs B B1-11 7.49 LF [matched by position]. Resolution: #2 A1 (A A1-10 / B B1-11) → **anexo (neither as list wall)** → A1-10 7.487 LF [R74.3 / R75.6 / E28(1)] → A02.01 (p.24) vector + dims 1'-10 3/4", 5'-6 1/2" → /home/user/boa29b/work/etapas/3_revision/res_img/R002.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R002.png
3/121 | Floor plan | A1 | Double-reading item 3 (Sheet A02.01 (p.24)): LF differs +1.38 LF (22.3 %): A A1-04 4.81 LF vs B B1-04 6.19 LF [matched by position]. Resolution: #3 A1 (A A1-04 / B B1-04) → **value** → A1-04 5.587 LF [R77.10 / R78.35 / R70.2] → A02.01 (p.24) dim 5'-0" + vector layer fills → /home/user/boa29b/work/etapas/3_revision/res_img/R003.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R003.png
4/121 | Floor plan | A1 | Double-reading item 26 (Sheet A02.01 (p.24)): only in reading B: B1-10 3.50 LF. Resolution: #26 A1 (A - / B B1-10) → **discard (duplicate)** → None 0 LF [R74.5 / E28 (one band = one wall)] → A02.01 (p.24) vector + PA0034 → /home/user/boa29b/work/etapas/3_revision/res_img/R026.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R026.png
5/121 | Floor plan | A1 | RFI-ADV-A101-BEHIND-C1: A1-01 face A (Waiting 104) behind the C1 monitor box A2-C1-05 (10'-0" x 8"): the A1 board behind the box is carried as well as the C1 face (correct by type, concealed). ¦ Delta: about -115 SF 5/8" board if the concealed A1 face behind the box is omitted | A02.01 | /home/user/boa29b/work/etapas/4_canon/img/adv/p24_C1_waiting.png
6/121 | Floor plan | A1K | RFI-ASM-K-CORNER: A02.01: the B2K Kevlar hatch of A2-B2K-01 is drawn to x 1655.40, 1.44 pt past the start face of A1-11 (x 1653.96, W tick of the printed 3'-5"). Take-off gives the corner to A1-11 (one owner, R70.2) and adds the jog y 1118.04-1120.68 at x 1653.96 (R76.3). Confirm the Kevlar panel is continuous around ¦ Delta: -0.08 ft x panel height per layer on A2-B2K-01: 3/8" ballistic panel -0.08 x 8.0 = -0.64 SF per layer; 5/8" board -0.08 x 15.375 = -1.23 SF per face per layer (jog adds back its own band, ball | A02.01 | /home/user/boa29b/work/etapas/3_revision/orq_img/k_zoom.png
7/121 | Floor plan | A5 | Double-reading item 4 (Sheet A02.01 (p.24)): LF differs -0.41 LF (8.3 %): A A1-16 4.87 LF vs B B1-17 4.47 LF [matched by position]. Resolution: #4 A5 (A A1-16 / B B1-17) → **A** → A1-16 4.873 LF [R78.35 / R70.2] → A02.01 (p.24) vector layer fills → /home/user/boa29b/work/etapas/3_revision/res_img/R004.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R004.png
8/121 | Floor plan | A5 | Double-reading item 5 (Sheet A02.01 (p.24)): LF differs +3.13 LF (22.1 %): A A1-15 11.00 LF vs B B1-16 14.13 LF [matched by position]. Resolution: #5 A5 (A A1-15 / B B1-16) → **B** → A1-15 14.127 LF [R77.9 / R77.10 / R78.35] → A02.01 (p.24) vector; A12.03 6/A12.03 B3-B4, 7/A12.03 → /home/user/boa29b/work/etapas/3_revision/res_img/R005.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R005.png
9/121 | Floor plan | B | RFI-ASM-BEAM-A2-B-02: A2-B-02: vigas_sobre_walls.py puts S2.20 W8X10 (axis 1509.85 pt) over 5.287 ft of the 11.719 ft wall (45.1 %); the record stops under the beam (E26 / R72.4). Confirm whether the studs outside the beam (6.432 ft) run to the deck. ¦ Delta: +0.657 ft per stud on the 6.432 ft outside the beam (@ 16" O.C., x 1 row(s)) and +0.657 ft x that length per board face to deck | 1/S2.20 | /home/user/boa29b/work/etapas/2_lectura/A_work/A6/img/p63_overview.png
10/121 | Floor plan | B | RFI-ASM-BEAM-A2-B-04: A2-B-04: vigas_sobre_walls.py finds an S2.20 beam line (axis 1586.43 pt) over 5.287 ft of the wall (45.1 %) with no W mark next to it (tool note: no W mark beside the beam, RFI with depth d): depth unknown, studs carried to deck. Confirm the member and whether the studs stop under it. ¦ Delta: -d (beam depth, ft) per stud on the 5.287 ft under the beam (@ 16" O.C.) and -d x 5.287 ft per board face to deck | 1/S2.20 | /home/user/boa29b/work/etapas/2_lectura/A_work/A6/img/p63_overview.png
11/121 | Floor plan | B2 | Double-reading item 6 (Sheet A02.01 (p.24)): LF differs +3.66 LF (24.3 %): A A2-B2-04 11.41 LF vs B B2-23 15.07 LF [matched by position]. Resolution: #6 B2 (A A2-B2-04,A1-17 / B B2-23,B1-18) → **A for B2 + value for A5 (door 116 single owner)** → A1-17 6.947 + A2-B2-04 11.407 LF [R75.5 / R70.3 / R77.10 / R78.31] → A02.01 (p.24) vector layer fills → /home/user/boa29b/work/etapas/3_revision/res_img/R006.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R006.png
12/121 | Floor plan | B2 | Double-reading item 7 (Sheet A02.01 (p.24)): LF differs +12.20 LF (43.6 %): A A2-B2-03 15.79 LF vs B B2-16 27.99 LF [matched by position]. Resolution: #7 B2 (A A2-B2-03 / B B2-16) → **A (B2 line = two walls, split by the alcove)** → A2-B2-03 15.787 LF [E28(1) / R74.3 / R75.6] → A02.01 (p.24) vector → /home/user/boa29b/work/etapas/3_revision/res_img/R007.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R007.png
13/121 | Floor plan | B2 | Double-reading item 12 (Sheet A02.01 (p.24)): only in reading A: A2-B2-02 5.54 LF. Resolution: #12 B2 (A A2-B2-02 / B -) → **A** → A2-B2-02 5.542 LF [E28(1) / R75.6] → A02.01 (p.24) dim 5'-6 1/2" → /home/user/boa29b/work/etapas/3_revision/res_img/R012.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R012.png
14/121 | Floor plan | B2K | Double-reading item 8 (Sheet A02.01 (p.24)): LF differs +0.96 LF (37.8 %): A A2-B2K-01 1.58 LF vs B B2-09 2.54 LF [matched by position]. Resolution: #8 B2K (A A2-B2K-01 / B B2-09) → **A** → A2-B2K-01 1.58 LF [R72.1 / R80.10] → A02.01 (p.24) vector hatch → /home/user/boa29b/work/etapas/3_revision/res_img/R008.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R008.png
15/121 | Floor plan | C1 | Double-reading item 9 (Sheet A02.01 (p.24)): LF differs -0.23 LF (7.1 %): A A2-C1-08 3.21 LF vs B B2-31 2.98 LF [matched by position]. Resolution: #9 C1 (A A2-C1-08 / B B2-31) → **value** → A2-C1-08 3.56 LF [R75.7 / R73.17] → A02.01 (p.24) vector layer fills → /home/user/boa29b/work/etapas/3_revision/res_img/R009.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R009.png
16/121 | Floor plan | C1 | Double-reading item 10 (Sheet A02.01 (p.24)): LF differs -0.63 LF (5.9 %): A A2-C1-05 10.63 LF vs B B2-28 10.00 LF [matched by position]. Resolution: #10 C1 (A A2-C1-05 / B B2-28) → **value** → A2-C1-05 11.333 LF [R75.7 / R73.17] → A02.01 (p.24) dims 10'-0", 8" → /home/user/boa29b/work/etapas/3_revision/res_img/R010.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R010.png
17/121 | Floor plan | C1 | Double-reading item 13 (Sheet A02.01 (p.24)): only in reading A: A2-C1-01 3.27 LF. Resolution: #13 C1 (A A2-C1-01 / B B2-24) → **A** → A2-C1-01 3.267 LF [R76.5 / E28(5)] → A02.01 (p.24) + A09.25 details 1 and 2 (p.40) → /home/user/boa29b/work/etapas/3_revision/res_img/R013.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R013.png
18/121 | Floor plan | C1 | Double-reading item 14 (Sheet A02.01 (p.24)): only in reading A: A2-C1-02 4.07 LF. Resolution: #14 C1 (A A2-C1-02 / B B2-25) → **A** → A2-C1-02 4.072 LF [R76.5 / E28(5)] → A02.01 (p.24) + A09.25 details 1 and 2 (p.40) → /home/user/boa29b/work/etapas/3_revision/res_img/R014.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R014.png
19/121 | Floor plan | C1 | Double-reading item 15 (Sheet A02.01 (p.24)): only in reading A: A2-C1-04 4.00 LF. Resolution: #15 C1 (A A2-C1-04 / B B2-27) → **B** → A2-C1-04 2.94 LF [R76.5 / R73.13] → A02.01 (p.24) vector + dim 1'-0" → /home/user/boa29b/work/etapas/3_revision/res_img/R015.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R015.png
20/121 | Floor plan | C1 | Double-reading item 27 (Sheet A02.01 (p.24)): only in reading B: B2-24 9.03 LF. Resolution: #27 C1 (A A2-C1-01 / B B2-24) → **same element as item 13 -> A** → A2-C1-01 3.267 LF [R76.5 / E28(5)] → A02.01 (p.24) + A09.25 details 1 and 2 (p.40) → /home/user/boa29b/work/etapas/3_revision/res_img/R027.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R027.png
21/121 | Floor plan | C1 | Double-reading item 28 (Sheet A02.01 (p.24)): only in reading B: B2-25 9.12 LF. Resolution: #28 C1 (A A2-C1-02 / B B2-25) → **same element as item 14 -> A** → A2-C1-02 4.072 LF [R76.5 / E28(5)] → A02.01 (p.24) + A09.25 details 1 and 2 (p.40) → /home/user/boa29b/work/etapas/3_revision/res_img/R028.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R028.png
22/121 | Floor plan | C1 | Double-reading item 29 (Sheet A02.01 (p.24)): only in reading B: B2-27 2.94 LF. Resolution: #29 C1 (A A2-C1-04 / B B2-27) → **same element as item 15 -> B** → A2-C1-04 2.94 LF [R76.5 / R73.13] → A02.01 (p.24) vector + dim 1'-0" → /home/user/boa29b/work/etapas/3_revision/res_img/R029.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R029.png
23/121 | Floor plan | EXT-6CFMF | RFI-ASM-BEAM-A3-W1: A3-W1: vigas_sobre_walls.py finds two parallel beams with different marks over the wall (W16X26 14.889 ft, W12X19 4.607 ft, W16X26 14.889 ft, W12X19 4.607 ft, W16X26 14.889 ft); the canon keeps stops_under_beam W12X19 (reading A); confirm which member the studs stop under (S2.20). ¦ Delta: per stud: height difference between the candidate beam depths (W12X19 1.017 ft, W16X26 1.308 ft) | 1/S2.20 | /home/user/boa29b/work/etapas/2_lectura/A_work/A6/img/p63_overview.png
24/121 | Floor plan | EXT-PARAPET | Double-reading item 19 (Sheet A02.01 (p.24)): only in reading A: A3-P-G 16.33 LF. Resolution: #19/#30 A3-P-G (N-HP, grid G 2->4, HP 4.292): 16.820 LF, base A3-PIER2+A3-PIER4, lf_override (over 12'-6 3/4" entrance storefront). A 16.333 / B 16.208 (CL-to-CL). | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/img/019_ONLYA_EXT-PARAPET_A02.01_p24.png
25/121 | Floor plan | EXT-PARAPET | Double-reading item 20 (Sheet A02.01 (p.24)): only in reading A: A3-P-F 39.86 LF. Resolution: #20/#32 A3-P-F (N, grid F 4->8, LP 2.042): 39.873 LF, base A3-N1, lf_override (over 26'-3" storefront). A 39.86 / B 40.0. | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/img/020_ONLYA_EXT-PARAPET_A02.01_p24.png
26/121 | Floor plan | EXT-PARAPET | Double-reading item 21 (Sheet A02.01 (p.24)): only in reading A: A3-P-8a+A3-P-8b 75.94 LF. Resolution: #21/#33 A3-P-8a + A3-P-8b (E, grid 8): 50.529 (2.042) + 24.911 (4.885) = 75.440, split at grid B (D9 roof step). A 75.94 / B 75.96 one run. | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/img/021_ONLYA_EXT-PARAPET_A02.01_p24.png
27/121 | Floor plan | EXT-PARAPET | Double-reading item 22 (Sheet A02.01 (p.24)): only in reading A: A3-P-A 52.33 LF. Resolution: #22/#34 A3-P-A (S, grid A 3->8, 4.885): 52.833 = S1a+S1b, one record. A/B 52.333. | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/img/022_ONLYA_EXT-PARAPET_A02.01_p24.png
28/121 | Floor plan | EXT-PARAPET | Double-reading item 23 (Sheet A02.01 (p.24)): only in reading A: A3-P-3a+A3-P-3b 47.93 LF. Resolution: #23/#35 A3-P-3a + A3-P-3b (W, grid 3): 22.516 (2.042) + 24.911 (4.885) = 47.427, split at grid B. A 47.927 / B 47.927 (B height PENDING -> resolved 4.885). | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/img/023_ONLYA_EXT-PARAPET_A02.01_p24.png
29/121 | Floor plan | EXT-PARAPET | Double-reading item 24 (Sheet A02.01 (p.24)): only in reading A: A3-P-D 3.86 LF. Resolution: #24/#36 A3-P-D (S-HP, grid D 2->3): 3.860 = SJ; HP 4.292 confirmed by 2/A09.02 (resolves B PENDING). A 3.86 / B 3.875. | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/img/024_ONLYA_EXT-PARAPET_A02.01_p24.png
30/121 | Floor plan | EXT-PARAPET | Double-reading item 25 (Sheet A02.01 (p.24)): only in reading A: A3-P-2 29.01 LF. Resolution: # Exterior resolution (items #17-#25, #30-#37 + EXT-6CFMF check) | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/img/025_ONLYA_EXT-PARAPET_A02.01_p24.png
31/121 | Floor plan | EXT-PARAPET | Double-reading item 30 (Sheet A02.02 (p.25)): only in reading B: B3-P01 16.21 LF. Resolution: # Exterior resolution (items #17-#25, #30-#37 + EXT-6CFMF check) | Sheet A02.02 (p.25) | /home/user/boa29b/work/etapas/3_revision/img/030_ONLYB_EXT-PARAPET_A02.02_p25.png
32/121 | Floor plan | EXT-PARAPET | Double-reading item 31 (Sheet A02.02 (p.25)): only in reading B: B3-P02 3.95 LF. Resolution: #31 A3-P-4R (N-HP, grid 4 return stub, HP 4.292): 3.678 LF, NEW for A; exists on 1/A02.02 key note 10 and 1/A09.02. B 3.947 (from G CL). | Sheet A02.02 (p.25) | /home/user/boa29b/work/etapas/3_revision/img/031_ONLYB_EXT-PARAPET_A02.02_p25.png
33/121 | Floor plan | EXT-PARAPET | Double-reading item 32 (Sheet A02.02 (p.25)): only in reading B: B3-P03 40.00 LF. Resolution: #20/#32 A3-P-F (N, grid F 4->8, LP 2.042): 39.873 LF, base A3-N1, lf_override (over 26'-3" storefront). A 39.86 / B 40.0. | Sheet A02.02 (p.25) | /home/user/boa29b/work/etapas/3_revision/img/032_ONLYB_EXT-PARAPET_A02.02_p25.png
34/121 | Floor plan | EXT-PARAPET | Double-reading item 33 (Sheet A02.02 (p.25)): only in reading B: B3-P04 75.96 LF. Resolution: #21/#33 A3-P-8a + A3-P-8b (E, grid 8): 50.529 (2.042) + 24.911 (4.885) = 75.440, split at grid B (D9 roof step). A 75.94 / B 75.96 one run. | Sheet A02.02 (p.25) | /home/user/boa29b/work/etapas/3_revision/img/033_ONLYB_EXT-PARAPET_A02.02_p25.png
35/121 | Floor plan | EXT-PARAPET | Double-reading item 34 (Sheet A02.02 (p.25)): only in reading B: B3-P05 52.33 LF. Resolution: #22/#34 A3-P-A (S, grid A 3->8, 4.885): 52.833 = S1a+S1b, one record. A/B 52.333. | Sheet A02.02 (p.25) | /home/user/boa29b/work/etapas/3_revision/img/034_ONLYB_EXT-PARAPET_A02.02_p25.png
36/121 | Floor plan | EXT-PARAPET | Double-reading item 35 (Sheet A02.02 (p.25)): only in reading B: B3-P06 47.93 LF. Resolution: #23/#35 A3-P-3a + A3-P-3b (W, grid 3): 22.516 (2.042) + 24.911 (4.885) = 47.427, split at grid B. A 47.927 / B 47.927 (B height PENDING -> resolved 4.885). | Sheet A02.02 (p.25) | /home/user/boa29b/work/etapas/3_revision/img/035_ONLYB_EXT-PARAPET_A02.02_p25.png
37/121 | Floor plan | EXT-PARAPET | Double-reading item 36 (Sheet A02.02 (p.25)): only in reading B: B3-P07 3.88 LF. Resolution: #24/#36 A3-P-D (S-HP, grid D 2->3): 3.860 = SJ; HP 4.292 confirmed by 2/A09.02 (resolves B PENDING). A 3.86 / B 3.875. | Sheet A02.02 (p.25) | /home/user/boa29b/work/etapas/3_revision/img/036_ONLYB_EXT-PARAPET_A02.02_p25.png
38/121 | Floor plan | EXT-PARAPET | Double-reading item 37 (Sheet A02.02 (p.25)): only in reading B: B3-P08 29.03 LF. Resolution: # Exterior resolution (items #17-#25, #30-#37 + EXT-6CFMF check) | Sheet A02.02 (p.25) | /home/user/boa29b/work/etapas/3_revision/img/037_ONLYB_EXT-PARAPET_A02.02_p25.png
39/121 | Floor plan | G | Double-reading item 11 (Sheet A02.01 (p.24)): LF differs -0.34 LF (2.7 %): A A2-G-01 12.67 LF vs B B2-10 12.33 LF [matched by position]. Resolution: #11 G (A A2-G-01 / B B2-10) → **B** → A2-G-01 12.333 LF [R74.1 / R74.2] → A02.01 (p.24) vector + dim 4" → /home/user/boa29b/work/etapas/3_revision/res_img/R011.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R011.png
40/121 | Floor plan | G | Double-reading item 16 (Sheet A02.01 (p.24)): only in reading A: A2-G-11 0.97 LF. Resolution: #16 G (A A2-G-11 / B -) → **A** → A2-G-11 0.973 LF [R74.1 / R74.2 / R78.35] → A02.01 (p.24) vector layer fills → /home/user/boa29b/work/etapas/3_revision/res_img/R016.png | Sheet A02.01 (p.24) | /home/user/boa29b/work/etapas/3_revision/res_img/R016.png
41/121 | Floor plan | G | RFI-ASM-BEAM-A2-G-01: A2-G-01: vigas_sobre_walls.py finds two parallel beams with different marks over the wall (W12X19 3.015 ft, W12X19 3.015 ft, W8X10 3.82 ft); the canon keeps studs to deck; confirm which member the studs stop under (S2.20). ¦ Delta: per stud: height difference between the candidate beam depths (W12X19 1.017 ft, W8X10 0.657 ft) | 1/S2.20 | /home/user/boa29b/work/etapas/2_lectura/A_work/A6/img/p63_overview.png
42/121 | Floor plan | G | RFI-ASM-BEAM-A2-G-02: A2-G-02: vigas_sobre_walls.py puts S2.20 W8X10 (axis 1040.57 pt) over 3.36 ft of the 11.625 ft wall (28.9 %); the record stops under the beam (E26 / R72.4). Confirm whether the studs outside the beam (8.265 ft) run to the deck. ¦ Delta: +0.657 ft per stud on the 8.265 ft outside the beam (@ 16" O.C., x 2 row(s)) and +0.657 ft x that length per board face to deck | 1/S2.20 | /home/user/boa29b/work/etapas/2_lectura/A_work/A6/img/p63_overview.png
43/121 | Floor plan | G | RFI-ASM-BEAM-A2-G-05: A2-G-05: vigas_sobre_walls.py puts S2.20 W14X30 (axis 1632.8 pt) over 1.795 ft of the 3.253 ft wall (55.2 %); the record stops under the beam (E26 / R72.4). Confirm whether the studs outside the beam (1.458 ft) run to the deck. ¦ Delta: +1.15 ft per stud on the 1.458 ft outside the beam (@ 16" O.C., x 2 row(s)) and +1.15 ft x that length per board face to deck | 1/S2.20 | /home/user/boa29b/work/etapas/2_lectura/A_work/A6/img/p63_overview.png
44/121 | Floor plan | G1 | RFI-ASM-BEAM-A2-G1-01: A2-G1-01: vigas_sobre_walls.py puts S2.20 W8X10 (axis 533.05 pt) over 3.354 ft of the 11.771 ft wall (28.5 %); the record stops under the beam (E26 / R72.4). Confirm whether the studs outside the beam (8.417 ft) run to the deck. ¦ Delta: +0.657 ft per stud on the 8.417 ft outside the beam (@ 16" O.C., x 2 row(s)) and +0.657 ft x that length per board face to deck | 1/S2.20 | /home/user/boa29b/work/etapas/2_lectura/A_work/A6/img/p63_overview.png
45/121 | Floor plan | G1 | RFI-ADV-G1-STUB: A2-G1-STUB (R74.2 stub, 4" faces) carries no board faces: it may be concealed by the vendor front jamb. ¦ Delta: about +20.5 SF 5/8" board (two 4" faces x 2 layers x 15.375) | A02.01 | /home/user/boa29b/work/etapas/4_canon/img/adv/p24_G1_stub.png
46/121 | Floor plan | OTHER FRAMING | RFI-A5-CARRY: RFI-A5-CARRY: direction of carrying channels in suspended GWB ceilings not shown; E-W assumed. Delta of N-S: 100 VESTIBULE: carrying 47.48 LF / 15 hangers (E-W) vs 37.98 LF / 15 hangers (N-S); 101 24 HR VESTIBULE: carrying 54.8 LF / 20 hangers (E-W) vs 47.82 LF / 20 hangers (N-S); 104 WAITING: carry ¦ Delta: Delta of N-S: 100 VESTIBULE: carrying 47.48 LF / 15 hangers (E-W) vs 37.98 LF / 15 hangers (N-S); 101 24 HR VESTIBULE: carrying 54.8 LF / 20 hangers (E-W) vs 47.82 LF / 20 hangers (N-S); 104 WAITI | A02.01 | /home/user/boa29b/work/etapas/2_lectura/A_work/A5/img/A5-C104_waiting.png
47/121 | Floor plan | OTHER FRAMING | RFI-A5-RR-DIFF: Restrooms 113/114: A04.01 shows two 2'x2' HVAC diffuser/grille symbols per room; M01.01 shows two single-section slot diffusers (TBDI-10, 2'-0") per room. Carried M01.01. Delta if 2'x2' framed: 4 x 2 x (2+2) = 32 LF vs slots 4 x 2 x 2.294 = 18.35 LF sides (+ends PENDING). ¦ Delta: Delta if 2'x2' framed: 4 x 2 x (2+2) = 32 LF vs slots 4 x 2 x 2.294 = 18.35 LF sides (+ends PENDING). | A02.01 | /home/user/boa29b/work/etapas/2_lectura/A_work/A5/img/A5-M01.01_SD_restrooms.png
48/121 | Floor plan | OTHER FRAMING | RFI-ASM-SLOPE-59-13: Sloped low zone grid B -> A (S2.20 13'-0 5/8" -> 12'-6 3/8", SLOPE): stud and board heights are carried at each wall's own high end (rule 59.13, interpolated). The older SKILL deck-height prose (zone high end for every wall) gives the alternative below; contradiction filed for the arbiter (morning-r ¦ Delta: if every low-zone wall is cut at the zone high end 13.0521: + dH ft per stud and per SF of board to deck: A1-05 +0.087, A1-06 +0.131, A1-07 +0.091, A1-08 +0.091, A1-09 +0.284, A1-10 +0.097, | A02.01 | /home/user/boa29b/work/etapas/4_canon/img/adv/S2.20_low_zone_BOD.png
49/121 | Floor plan | OTHER FRAMING | RFI-ASM-BEAM-A3-SFC-F: A3-SFC-F: vigas_sobre_walls.py finds two parallel beams with different marks over the wall (W16X26 26.242 ft, W16X26 26.242 ft, W18X35 26.242 ft, W16X26 26.242 ft); the canon keeps stops_under_beam W18X35 (reading A); confirm which member the studs stop under (S2.20). ¦ Delta: per stud: height difference between the candidate beam depths (W16X26 1.308 ft, W18X35 1.475 ft) | 1/S2.20 | /home/user/boa29b/work/etapas/2_lectura/A_work/A6/img/p63_overview.png
50/121 | Floor plan | OTHER FRAMING | RFI-ADV-TA: A08.01 legend: TA-2 / TA-13 / TA-14 are recessed but their rough-opening widths are not printed. 0 carried (R71.6). Provide the R.O. of each (spec Div 10). ¦ Delta: TA-13 x2 (vector 17.16" > stud bay 14 3/8"): +5.53 LF header (single track) and +5.53 LF sill track; TA-2 (13.0") and TA-14 (14.08") fit the bay: 0 | A02.01 | /home/user/boa29b/work/etapas/4_canon/img/adv/A0801_TA_legend.png
51/121 | Floor plan | OTHER FRAMING | RFI-ADV-WC20: WC-20 (A05.01 key note 9, 24 HR Vestibule 101): not in the A00.40 finish legend; extent taken from the leaders at both ends of the diagonal ATM wall, height to the GB 10'-0" ceiling (53.3). Confirm extent and height. ¦ Delta: per ft of height: -15.208 SF Level 5 per ft below the ceiling (e.g. to 8'-0": -30.416 SF) | A02.01 | /home/user/boa29b/work/etapas/4_canon/img/adv/A0501_vest101_kn9.png
52/121 | Floor plan | OTHER FRAMING | RFI-ADV-A0031: A05.01 notes A/B and A03.01 note D refer to the FINISH SCHEDULE A00.31; A00.31 is not in the bid set nor in the A00.00 index. It may change the extents of FRP, Level 5 and wallcoverings. ¦ Delta: not quantifiable until A00.31 is issued | A02.01 | /home/user/boa29b/work/etapas/4_canon/img/adv/A0501_notes_A00_31.png
53/121 | Floor plan | OTHER FRAMING | RFI-ADV-A0812: A00.60 site note 13 'DRIVE UP ATM. SEE A03.01 & A08.12': A08.12 does not exist in the set (probably A08.11). Confirm. ¦ Delta: none if A08.11 is the intended sheet (drive-up ATM already from 5/A08.11 and 6/A08.11) | A02.01 | /home/user/boa29b/work/etapas/4_canon/img/adv/A0060_note13_A0812.png
54/121 | Floor plan | OTHER FRAMING | RFI-ADV-HAT: A09.31: 7/8" hat channel @ 16" O.C. behind the EPS-5 formed metal panel and the composite metal panel: not counted, not excluded. Proposed as panel subcontractor subframing (Div 07) in Clarifications. ¦ Delta: not quantified (Div 07 subframing) | A02.01 | /home/user/boa29b/work/etapas/4_canon/img/adv/p42_det15_driveup.png
55/121 | Floor plan | OTHER FRAMING | RFI-ADV-SIGNAGE: A08.01 KN3 restroom signage 'installed by GC' and A02.01 KN12 wellness signage: no blocking counted (adhesive mount assumed). ¦ Delta: +1.333 LF metal blocking per sign if mechanically fastened | A02.01 | /home/user/boa29b/work/etapas/4_canon/img/adv/A0801_TA_legend.png
56/121 | Floor plan | OTHER FRAMING | A4-RFI-103-SCHED: A4-RFI-103-SCHED: A00.30 row 103 HEIGHT 13'-6 1/2" vs grille R.O. 13'-4" wide / ~10'-0" high (A02.01, A08.21); no LF delta in header (width from A02.01) ¦ Delta: 0 LF: header width taken from A02.01; schedule height conflict only | A02.01
57/121 | Floor plan | OTHER FRAMING | A4-RFI-FEC1: A4-RFI-FEC1: FEC-1 recessed cabinet size not printed (A00.40 size '-', spec 10 44 00). 0 carried; delta if R.O. > stud bay 14 3/8": header + sill (R.O. + 1'-4") x 2 per cabinet ¦ Delta: + (R.O. + 1'-4") x 2 LF per cabinet if R.O. > stud bay; 0 carried | A02.01
58/121 | Floor plan | OTHER FRAMING | A4-RFI-TA: A08.01 TOILET ACCESSORY LEGENDS designate TA-2 RECESSED PAPER TOWEL DISPENSER, TA-13 HAND DRYER W/ ADA COMPLIANT RECESS KIT and TA-14 RECESSED WASTE RECEPTACLE (rows above, width not printed -> 0 + RFI-ADV-TA, R71.6); the other TA items carry no recessed designation ¦ Delta: n/a: recessed accessory sizes per cutsheet; framed openings carried per sweep | A02.01
59/121 | Floor plan | OTHER FRAMING | RFI-FO-R-11C-1: RFI R-11C: opening width not printed (E00.01 light fixture schedule (R-11C description / catalog FSM2L-...-TF-XF2 give no opening width)); Provide opening width for the recessed linear gyp slot (cutsheet); framing ends not carried; ends not carried ¦ Delta: +2 x W x 2 LF (ends; W pending) | A02.01
60/121 | Floor plan | OTHER FRAMING | RFI-FO-R-11C-2: RFI R-11C: schedule description 12.0 ft vs catalog 20.0 ft; carried 12.0 ft (desc = drawn); alternate 20.0 ft ¦ Delta: +32 LF | A02.01
61/121 | Floor plan | OTHER FRAMING | RFI-FO-R-11CE-3: RFI R-11CE: opening width not printed (E00.01 light fixture schedule (R-11CE 'SAME AS ABOVE' - no opening width)); Provide opening width for the recessed linear gyp slot (cutsheet); framing ends not carried; ends not carried ¦ Delta: +2 x W x 2 LF (ends; W pending) | A02.01
62/121 | Floor plan | OTHER FRAMING | RFI-FO-R-11CE-4: RFI R-11CE: schedule description 12.0 ft vs catalog 20.0 ft; carried 12.0 ft (desc = drawn); alternate 20.0 ft ¦ Delta: +32 LF | A02.01
63/121 | Floor plan | OTHER FRAMING | RFI-FO-SD-3SEC-6: RFI SD-3SEC: opening width not printed (M00.03 schedule 'SD/SDR TITUS TBDI-10 ... (2) 1" SLOTS', size 'SEE DRAWING' - opening width not printed (drawn outer ~7.7")); Provide slot diffuser TBDI-10 2-slot frame width for the GWB opening; ends not carried; ends not carried ¦ Delta: +2 x W x 4 LF (ends; W pending) | A02.01
64/121 | Floor plan | OTHER FRAMING | RFI-FO-SD-1SEC-7: RFI SD-1SEC: opening width not printed (M00.03 'SD/SDR TITUS TBDI-10 (2) 1" SLOTS', size 'SEE DRAWING' - width not printed); Provide TBDI-10 frame width; A04.01 shows 2'x2' diffuser symbols in the restrooms instead of slots - confirm device; ends not carried ¦ Delta: +2 x W x 4 LF (ends; W pending) | A02.01
65/121 | Floor plan | OTHER FRAMING | RFI-CR-BRACING: RFI bracing: 123.04 LF of C.R. channel bracing runs across openings without studs (53.4, literal). ¦ Delta: -123.04 LF of C.R. channel if not run across openings | A02.01
66/121 | Floor plan | OTHER FRAMING | RFI-CR-DOORS: RFI bottom track: 50.5 LF of door R.O. are NOT deducted from the bottom track (corridas.py). ¦ Delta: -50.5 LF of bottom track if door R.O. are deducted | A02.01
67/121 | Floor plan | OTHER FRAMING | RFI-L5-WC20: RFI-ADV-WC20: WC-20 height / extent not printed ¦ Delta: n/a: Level 5 SF changes with the WC-20 extent (L x (10'-0" - base) on that face) | A02.01
68/121 | Floor plan | OTHER FRAMING | RFI-ACCESS-PANELS: M00.01 general note 16 'PROVIDE ACCESS PANELS FOR ALL EQUIPMENT, DAMPERS ... ABOVE INACCESSIBLE CEILINGS' gives no count: M/P sweep against the GWB ceilings (restrooms, waiting, vestibules, CSR soffit) pending. ¦ Delta: +1 access panel per inaccessible item found (1 carried) | A02.01
69/121 | Floor plan | OTHER FRAMING | RFI-BLK-NOTE-C: Blocking at wall-mounted items per general note C (23 items): note C gives no material; metal 362CR stud blocking carried (58.6) ¦ Delta: 0 LF: material swap only (the same LF moves from metal stud blocking to the FRT blocking row) | A02.01
70/121 | Floor plan | OTHER FRAMING | RFI-BLK-36: A7-B-WS: Wall stop blocking material and length not printed: metal 362CR stud blocking one bay per stop assumed; delta to FRT 2x = same LF in the FRT family. ¦ Delta: delta to FRT 2x = same LF in the FRT family. | A02.01
71/121 | Floor plan | OTHER FRAMING | RFI-SHEET-LEN: 56.8: blocking location not given; carried at the horizontal board joint of faces taller than 12 ft; alternative (a) exterior walls + double-layer types ¦ Delta: n/a: blocking LF moves to the alternative location (exterior walls + double-layer types) | A02.01
72/121 | Floor plan | SF-PIER | Double-reading item 17 (Sheet A02.01 (p.24)): only in reading A: A3-PIER2 9.07 LF. Resolution: # Exterior resolution (items #17-#25, #30-#37 + EXT-6CFMF check) | Sheet A02.01 (p.24)
73/121 | Floor plan | SF-PIER | Double-reading item 18 (Sheet A02.01 (p.24)): only in reading A: A3-PIER4 9.08 LF. Resolution: #18 SF-PIER A3-PIER4 / C1 A2-C1-02 (PT0030) / B2-25: C1 = 4.072 LF interior; A3-PIER4 exterior part (part_of A2-C1-02, 2/A09.25) = N 2.5625 + E 1.422 = 3.984 LF. Removes A 9.076 and B C1 9.12. | Sheet A02.01 (p.24)
74/121 | Detail | 24 | RFI-ADV-PF06: PF-06 wall-hung bi-level fountain (P00.01, no carrier): A02.01 note C requires blocking, no material printed. Carried 3.13 LF metal stud blocking (58.6). ¦ Delta: material only: 3.13 LF metal -> FRT (same LF) | 1/A08.01 | /home/user/boa29b/work/etapas/4_canon/img/adv/P0001_PF06_schedule.png
75/121 | Detail | 25 | A4-RFI-ATM-DU-RO: A4-RFI-ATM-DU-RO: DU ATM R.O. width 2'-2 1/2" (7/A08.11) vs 2'-2 1/8" (26.4") (5/A08.11). Delta header + sill track = 3/8" x (4 box pieces + 1 sill) = 0.16 LF ¦ Delta: Delta header + sill track = 3/8" x (4 box pieces + 1 sill) = 0.16 LF | 7/A08.11
76/121 | Detail | 52 | RFI-TYPE-B2K: B2K is tagged on A02.01 (PC0011) but has no row in the A12.01 schedule: carried as B2 + Kevlar per 4/A12.01 [DERIVED], declare in Clarifications ¦ Delta: n/a: carried as B2 + Kevlar per 4/A12.01; any other build-up changes the B2K row only | 4/A12.01
77/121 | Detail | 52 | RFI-TYPE-G-GAUGE: G / G1 types: 1-5/8" stud designation / gauge not scheduled ¦ Delta: n/a: gauge only (LF unchanged) | 5/A12.01
78/121 | Detail | 52 | Assumption: board height per face = scheduled ceiling + 6" (3/A12.01 note) or to deck where the room is open to structure. | 3/A12.01
79/121 | Detail | 52 | Assumption: B2K (tag on A02.01, not in the A12.01 schedule) carried as B2 + Kevlar build-up per 4/A12.01. | 4/A12.01
80/121 | Detail | 53 | A4-RFI-VEST-BOX: A4-RFI-VEST-BOX: 'BOX HEADER AS NEEDED' (4-7/A12.10) size / members not printed (E11). Counted as 4 pieces x (R.O. + 1'-4"); confirm member size ¦ Delta: n/a: member size only (piece count and LF carried: 4 pieces x (R.O. + 1'-4")) | 7/A12.10
81/121 | Detail | 54 | RFI-BLK-54: A7-B-LOCKERS: Locker width differs between 5/A11.02 (3.75 ft) and the dashed plan footprint (~4.9 ft); rows and material not printed (metal assumed). Delta +1.15 LF. ¦ Delta: Delta +1.15 LF | 5/A11.02
82/121 | Detail | 75 | A4-RFI-ATM-DU-OC: A4-RFI-ATM-DU-OC: O.C. of the 2 1/2" sistered studs and of the furring at the DU ATM recess not printed (6/A08.11); 16" O.C. carried. Delta at 24" O.C.: sistered 2 x 6.0 = 12.0 (-6.0 LF); furring 3 x 2.87 = 8.62 (-5.75 LF) ¦ Delta: Delta at 24" O.C | 6/A08.11
83/121 | Detail | 75 | Assumption: ATM recess sistered studs and furring at 16" O.C. (not printed). | 6/A08.11
84/121 | Detail | 76 | RFI-A3-PIER-STUDS: Storefront pier studs_drawn (1/A09.25, 2/A09.25) counted visually - verify. ¦ Delta: n/a: studs drawn in 1/A09.25 and 2/A09.25 counted from the drawing | 1/A09.25
85/121 | Detail | 76 | RFI-PLY-2: 1/A09.25: two hatched 3/4" plies drawn at the jamb but the label is singular '3/4" FRT PLYWOOD': 1 ply carried (label); second ply delta +12.903 SF ¦ Delta: delta +12.903 SF | 1/A09.25
86/121 | Detail | 76 | RFI-PLY-3: 2/A09.25: two hatched 3/4" plies drawn at the jamb but the label is singular '3/4" FRT PLYWOOD': 1 ply carried (label); second ply delta +6.452 SF ¦ Delta: delta +6.452 SF | 2/A09.25
87/121 | Detail | 76 | RFI-PLY-4: 2/A09.25: two hatched 3/4" plies drawn at the jamb but the label is singular '3/4" FRT PLYWOOD': 1 ply carried (label); second ply delta +4.25 SF ¦ Delta: delta +4.25 SF | 2/A09.25
88/121 | Detail | 101 | RFI-BLK-62: A7-B-WH1: NTS detail: length per row not printed (one stud bay assumed); 2X without FRT label = wood (R76.7). ¦ Delta: n/a: one row length per item; LF changes with the printed length | 3/P00.01
89/121 | Detail | 302 | RFI-ADV-RS1-FACE: 4/A02.02: an unlabelled gypsum-hatched layer is drawn on the inner (high-roof) face of RS-1 from the blocking down to the high deck (~1.0 ft). Not carried (no label). ¦ Delta: about +52 SF 5/8" exterior gypsum sheathing (51.594 x 1.0) | 4/A02.02 | /home/user/boa29b/work/etapas/4_canon/img/adv/p25_det4_top.png
90/121 | Detail | 302 | RFI-ADV-RS-BEAD: Roof step bottom closure (4/A02.02): corner bead at the two open bottom edges not labelled. Not carried. ¦ Delta: +103.2 LF corner bead (2 x 51.594) if required | 4/A02.02 | /home/user/boa29b/work/etapas/4_canon/img/adv/p25_det4_bottom.png
91/121 | Detail | 302 | RFI-A3-HP-BACK: HP parapet block (T.O. PARAPET 2 20'-0") back faces: A09.02 south/east elevations show key note 7 'EXTERIOR PROTECTION BOARD' on the back of the block over grids 2-4 / D-F, but A02.02 roof plan draws no parapet on grid 4 (D->F) nor grid D (3->4). Not quantified; delta ~ (3.9 + 27) ft x 4.29 ft parap ¦ Delta: +(3.9 + 27) ft x 4.29 ft of parapet back face if the HP block back faces exist (not carried) | 1/A02.02
92/121 | Detail | 302 | RFI-BLK-74: A6-B-HATCH: RFI-ADV-HATCH: hatch size not printed (drawn outline measured). ¦ Delta: n/a: one row length per item; LF changes with the printed length | 1/A02.02
93/121 | Detail | 304 | RFI-ADV-MW08: MW08 blocking: 3/A12.04 (called on 10/A12.04 at the microwave niche) reads PRESSURE TREATED and draws 2 rows; sheet note D (A12.03-A12.06) reads FRTW. Carried FRT x 2 rows over the 7'-7" counter. Confirm material and whether the second row runs the full counter or only the 2'-5" niche. ¦ Delta: material: 15.17 LF FRT -> pressure-treated wood (no LF change); rows: if the second row is only at the niche, -5.17 LF (7.583 - 2.417) | 3/A12.04 | /home/user/boa29b/work/etapas/4_canon/img/adv/A1204_3_counter_shelving.png
94/121 | Detail | 304 | RFI-ADV-SHELF-ROWS: 11/A12.04 SECTION @ SHELVING OVERHEAD draws 2 blocking pieces per unit; the canon carries one row per mounting level for MW12 / MW05 / MW06A / MW13. ¦ Delta: MW12 +7.0 LF; MW05 +3.5, MW06A +6.92, MW13 +11.67 LF FRT if 2 rows each | 11/A12.04 | /home/user/boa29b/work/etapas/4_canon/img/adv/A1204_11_shelving_overhead.png
95/121 | Detail | 304 | RFI-ADV-MW13-CITE: A7-B-MW13 op quotes 'PRESSURE TREATED' (text of 3/A12.04); A12.06 says 'PROVIDE ADDITIONAL BLOCKING' with no material. Citation to be reviewed; material stays FRT per sheet note D. ¦ Delta: none (citation only) | 3/A12.04 | /home/user/boa29b/work/etapas/4_canon/img/adv/A1204_3_counter_shelving.png
96/121 | Detail | 304 | RFI-BLK-30: A7-B-MW08: RFI-ADV-MW08: 3/A12.04 says 'PROVIDE ADDITIONAL PRESSURE TREATED BLOCKING IN PARTITION' while sheet note D says FRTW; carried FRT (sheet note label). 3/A12.04 is cut at the microwave niche (2'-5" HOLD). ¦ Delta: n/a: one row length per item; LF changes with the printed length | 3/A12.04
97/121 | Detail | 620 | RFI-ASM-MEP-P: Plumbing sheets P01.01 / P01.02 / P02.01 and M01.02 / M02.01 do not register against A02.01 with >= 25 wall-segment votes (mep.py): their pipe / duct crossings of stud walls are not counted geometrically; confirm pipes > 1" through stud webs (6/S5.20 plate each). ¦ Delta: +1 plate per stud cut per pipe > 1" crossing a stud wall (count not available without registration) | 6/S5.20 | /home/user/boa29b/work/etapas/4_canon/img/mep_overview.png
98/121 | Detail | 620 | A4-RFI-CSR-HDR: A4-RFI-CSR-HDR: header over the 12'-0 1/4" CSR line R.O. (Cash Window 116) not shown; 7/S5.20 tops at 8'-0". If a metal stud box beam (4 pieces): (12.0208 + 1.3333) x 4 = 53.42 LF of header ¦ Delta: +53.42 LF header if a 4-piece metal stud box beam is required (not carried) | 7/S5.20
99/121 | Detail | 921 | RFI-TRIM-3: Grille-side bottom corner assumed beaded (TYP.); delta -13.333 LF if only the room side is exposed. ¦ Delta: delta -13.333 LF if only the room side is exposed | 4/A08.21
100/121 | Detail | 921 | RFI-BLK-70: A7-B-GRILLE: Second jamb assumed mirrored (detail 3 'TYP'); height measured in vector (no printed height). ¦ Delta: n/a: one row length per item; LF changes with the printed length | 3/A08.21
101/121 | Detail | 1001 | Assumption: elevation titles N/S swapped vs the plan north arrow (A09.01 'SOUTH ELEVATION' = plan north); the plan north arrow was used for every facade. | 1/A09.01
102/121 | Detail | 1002 | RFI-ADV-4R-FACE: Tower return 4R: the east face south of F (~2.7 ft) also faces the roof; only one roof-side face is carried. ¦ Delta: about +11.5 SF exterior gypsum or about +6 SF nailbase | 1/A09.02 | /home/user/boa29b/work/etapas/4_canon/img/adv/p25_tower_return_4R.png
103/121 | Detail | 1021 | RFI-A3-CANOPY-BEAM: Canopy beams (W16x26/W12x19 CANOPY, HSS10x3 CANOPY) inside the exterior stud cavity (C/A09.21, H/A09.23, 15/A09.27): walls kept continuous to the HI/LOW roof beam (R80.2); split = +track, -stud. ¦ Delta: split = +1 track line per beam run, -stud length above the beam (R80.2) | C/A09.21
104/121 | Detail | 1026 | RFI-ADV-GM-BAND: Canopy glass-mat band height: 3/A09.26 nailbase hatch stops at y 501.5 and resumes at y 643.2 = 1.31 ft on the wall (scale checked on the 6" dim); the canon keeps the estimator formula E25 T/STUD - B/STUD = 1.979 ft (fascia elevations). ¦ Delta: if the wall geometry is used: glass mat -86.2 SF (129.03 LF x 0.668), nailbase +124.1 SF (185.8 LF x 0.668) | 3/A09.26 | /home/user/boa29b/work/etapas/4_canon/img/adv/p41_det3_zoom.png
105/121 | Detail | 1026 | RFI-ADV-CAN-HANGERS: Canopy soffit vertical members: 3/A09.26 (and 7/A09.26) draw two 3 5/8" dashed verticals (~0.86 ft) from the canopy steel to the soffit joist; spacing not printed. Not carried. ¦ Delta: about +84 LF 3 5/8" CFMF on the N canopy (one pair per joist: (15 + 34) x 2 x 0.86); E/S/W in proportion | 3/A09.26 | /home/user/boa29b/work/etapas/4_canon/img/adv/p41_det3_zoom.png
106/121 | Detail | 1027 | RFI-ADV-DU-BAND: Drive-up canopy band (W, W-HP, S-HP; 15/A09.27): a dashed sheathing line is drawn on the stud face behind the canopy but not labelled (the 3/A09.26 band labels 5/8" GLASS-MAT SHEATHING). Carried none (R78.13). Confirm. ¦ Delta: +112.3 SF 5/8" glass mat if sheathed (56.751 LF x 1.979) | 15/A09.27 | /home/user/boa29b/work/etapas/4_canon/img/adv/p42_det15_driveup.png
107/121 | Detail | 1027 | A4-RFI-SUBSTRATE-WIDTH: A4-RFI-SUBSTRATE-WIDTH: constants.opening_substrate_width_ft (strip width of the 3/4" FRT plywood at heads / jambs of windows, storefronts and door 123) not dimensioned in 11/A09.27, 2/A09.26, 14/A09.27, 3/A09.25, 4/A09.25 -> estimator criterion ¦ Delta: n/a: strip width is an estimator criterion; SF of 3/4" FRT plywood substrate scales with the width | 11/A09.27
108/121 | Detail | 1027 | RFI-A3-CANOPY-JOIST: Drive-up canopy soffit 3 5/8" joists spanning up to 21'-6" (16/A09.27) - support / direction RFI. ¦ Delta: n/a: support / direction only; joist LF carried per 16/A09.27 | 16/A09.27
109/121 | Detail | 1030 | RFI-ADV-HATCH: Roof hatch (A02.02 key note 8, 1/A09.30): size not printed; drawn outline 2.833 x 3.433 ft used for the 2x FRT curb blocking (2 plies). Confirm the hatch model / curb size. ¦ Delta: per inch of hatch size: +2 x 2 plies x 1/12 ft = +0.333 LF FRT blocking per inch on each side dimension | 1/A09.30 | /home/user/boa29b/work/etapas/4_canon/img/adv/A0202_roof_hatch.png
110/121 | Detail | 1030 | RFI-BLK-61: A7-B-LADDER: Bracket count follows the 3 levels drawn (the elevation has a break line); blocking length per level = printed ladder width min. 1'-6". ¦ Delta: n/a: one row length per item; LF changes with the printed length | 3/A09.30
111/121 | Detail | 1033 | RFI-A5-VS: Vertical studs of 7/A09.33 transitions: spacing not printed; 16" O.C. carried (8/A09.33). Delta @24": Waiting transitions 77.03 LF. ¦ Delta: Delta @24": Waiting transitions 77.03 LF. | 7/A09.33 | /home/user/boa29b/work/etapas/4_canon/img/A09.33_det7.png
112/121 | Detail | 1033 | RFI-A5-CSR: 10/A09.33 draws a scheduled partition on one side of the CSR soffit; 4/A12.08 shows ACT-4 9'-0" on both sides. Carried 2 drop lines (soffit_side both sides). Delta if one side is a partition: -2 soffit_side segments on that side (12.02 LF track x2, studs). ¦ Delta: Delta if one side is a partition: -2 soffit_side segments on that side (12.02 LF track x2, studs). | 10/A09.33 | /home/user/boa29b/work/etapas/2_lectura/A_work/A5/img/A5-CSR_4_A12.08.png
113/121 | Detail | 1033 | RFI-ADV-CAN-SHEATH: Canopy soffit sheathing: 4/A09.33 and 5/A09.33 say '5/8" EXTERIOR SHEATHING' while 3/A09.26, 7/A09.26, 16/A09.27 say '5/8" EXT. GRADE FRT PLYWOOD'. Carried plywood. ¦ Delta: material only (no SF change) | 4/A09.33 | /home/user/boa29b/work/etapas/4_canon/img/adv/p45_det4_5_canopy_light.png
114/121 | Detail | 1033 | RFI-FO-R-11A-5: RFI R-11A: opening width not printed (E00.01 schedule R-11A gives no width; 6/A09.33 trimless detail (bubbled in 10/A09.33) prints no opening width); Provide opening width for the recessed linear gyp slot (cutsheet); framing ends not carried; ends not carried ¦ Delta: +2 x W x 2 LF (ends; W pending) | 6/A09.33
115/121 | Detail | 1033 | RFI-FO-UU1-8: RFI UU1: opening width not printed (5/A09.33 + 4/A09.33 'CANOPY LINEAR LIGHT DETAIL - TRANS': width 'COORD. W/ FIXTURE CUTSHEET' (not printed); E00.01 catalog LSR-WET-2.5 is a model code, not an opening width); Provide the recess width of the Coronet LSR-WET UU1 (20.0' fixture) in the 5/8" exterior ¦ Delta: +2 x W x 1 LF (ends; W pending) | 4/A09.33
116/121 | Detail | 1033 | RFI-FO-UU2-9: RFI UU2: opening width not printed (5/A09.33 + 4/A09.33 'CANOPY LINEAR LIGHT DETAIL - TRANS': width 'COORD. W/ FIXTURE CUTSHEET' (not printed); E00.01 catalog LSR-WET-2.5 is a model code, not an opening width); Provide the recess width of the Coronet LSR-WET UU2 (2.0' fixture) in the 5/8" exterior s ¦ Delta: +2 x W x 5 LF (ends; W pending) | 4/A09.33
117/121 | Detail | 1033 | RFI-FO-UU3-10: RFI UU3: opening width not printed (5/A09.33 + 4/A09.33 'CANOPY LINEAR LIGHT DETAIL - TRANS': width 'COORD. W/ FIXTURE CUTSHEET' (not printed); E00.01 catalog LSR-WET-2.5 is a model code, not an opening width); Provide the recess width of the Coronet LSR-WET UU3 (3.0' fixture) in the 5/8" exterior s ¦ Delta: +2 x W x 9 LF (ends; W pending) | 4/A09.33
118/121 | Detail | 1033 | RFI-FO-UU4-11: RFI UU4: opening width not printed (5/A09.33 + 4/A09.33 'CANOPY LINEAR LIGHT DETAIL - TRANS': width 'COORD. W/ FIXTURE CUTSHEET' (not printed); E00.01 catalog LSR-WET-2.5 is a model code, not an opening width); Provide the recess width of the Coronet LSR-WET UU4 (55.0' fixture) in the 5/8" exterior ¦ Delta: +2 x W x 4 LF (ends; W pending) | 4/A09.33
119/121 | Detail | 1033 | RFI-FO-UU5-12: RFI UU5: opening width not printed (5/A09.33 + 4/A09.33 'CANOPY LINEAR LIGHT DETAIL - TRANS': width 'COORD. W/ FIXTURE CUTSHEET' (not printed); E00.01 catalog LSR-WET-2.5 is a model code, not an opening width); Provide the recess width of the Coronet LSR-WET UU5 (50.0' fixture) in the 5/8" exterior ¦ Delta: +2 x W x 1 LF (ends; W pending) | 4/A09.33
120/121 | Detail | 1033 | RFI-FO-UU6-13: RFI UU6: opening width not printed (5/A09.33 + 4/A09.33 'CANOPY LINEAR LIGHT DETAIL - TRANS': width 'COORD. W/ FIXTURE CUTSHEET' (not printed); E00.01 catalog LSR-WET-2.5 is a model code, not an opening width); Provide the recess width of the Coronet LSR-WET UU6 (16.0' fixture) in the 5/8" exterior ¦ Delta: +2 x W x 1 LF (ends; W pending) | 4/A09.33
121/121 | Detail | 1033 | Assumption: transition vertical studs at 16" O.C. (8/A09.33) where 7/A09.33 prints no spacing. | 7/A09.33

## Scope Checklist
Scope ID | Scope | Status | Note (quantity, NOT APPLICABLE + sheet, or RFI)
ALC-01 | Interior partition framing (studs + tracks) | QUANTIFIED | familias_out.json '3-5/8" stud (all gauges)' 7018.1; familias_out.json '6" stud (all gauges)' 4490.17; familias_out.json '1-5/8" stud' 4052.22 (3/A12.01)
ALC-02 | Exterior wall framing (CFMF) | QUANTIFIED | familias_out.json '6" stud (all gauges)' 4490.17 (C/A09.21)
ALC-03 | Parapet framing | QUANTIFIED | familias_out.json '6" parapet stud' 1014.52 (4/A09.26)
ALC-04 | Top / deflection and bottom track | QUANTIFIED | familias_out.json 'bottom track (all)' 1354.93; familias_out.json 'top / deflection track (all)' 1354.93 (3/A12.01)
ALC-05 | Headers, sills and jambs at openings | QUANTIFIED | familias_out.json 'header / box beam' 796.71; familias_out.json 'sill track' 119.12 (8/A12.01)
ALC-06 | Bracing / bridging | QUANTIFIED | familias_out.json 'bracing C.R. channel' 2516.87 (3/A12.01)
ALC-07 | Gypsum board on walls (layers per type) | QUANTIFIED | familias_out.json '5/8" gyp board regular (walls + ceilings)' 17364.3 (3/A12.01)
ALC-08 | Moisture / abuse / special board at wet zones | QUANTIFIED | familias_out.json '5/8" gyp MOISTURE RESISTANT' 258.81 (A08.01)
ALC-09 | Exterior gypsum / glass mat sheathing | QUANTIFIED | familias_out.json '5/8" EXTERIOR gyp sheathing' 961.09; familias_out.json '5/8" glass mat sheathing' 368.75 (C/A09.21)
ALC-10 | FRT plywood sheathing / substrate | QUANTIFIED | familias_out.json 'FRT plywood (SF)' 6771.17 (3/A09.26)
ALC-11 | Gypsum board ceilings | QUANTIFIED | familias_out.json '5/8" gyp board regular (walls + ceilings)' 17364.3 (A04.01)
ALC-12 | Ceiling suspension (furring / carrying channel / hanger wire / ceiling track) | QUANTIFIED | familias_out.json 'furring channel' 779.51; familias_out.json 'carrying channel' 323.56; familias_out.json 'hanger wire' 530.15; familias_out.json 'ceiling / soffit track' 1298.75 (8/A09.33)
ALC-13 | Soffits and bulkheads (framing + board) | QUANTIFIED | familias_out.json 'ceiling / soffit track' 1298.75 (9/A12.08)
ALC-14 | Canopy / marquee framing and sheathing | QUANTIFIED | Track, ceilings / soffits / canopy + FRT plywood sheathing (canopy and soffits) + canopy column wraps (3/A09.26)
ALC-15 | Column furring / wraps | QUANTIFIED | CANOPY-COL column wraps (Partition Takeoff) + 5/8" FRT plywood at canopy column wraps (5/A09.25)
ALC-16 | Blocking (FRT wood / metal) for millwork and accessories | QUANTIFIED | familias_out.json 'FRT blocking' 1006.63; familias_out.json 'metal stud blocking (362CR / STUD BLOCKING)' 649.32 (1/A08.01)
ALC-17 | Framed openings (MEP, access panels, diffusers) | QUANTIFIED | framed_openings_out.json 'framed openings MEP' 928.25 LF + access panel 1 PCS (E00.01 / M01.01)
ALC-18 | Trim: corner bead, casing bead, control joints, reveals | QUANTIFIED | familias_out.json 'metal trim (corner bead, casing, shadow molding)' 1041.42 (7/A09.33)
ALC-19 | Acoustical sealant / sound attenuation (EXCLUDED: estimator standing order, all projects) | NOT APPLICABLE | EXCLUDED: EXCLUDED in all projects (estimator standing order): no acoustical sealant row and no quantity
ALC-20 | FRP / cement board / tile backer | QUANTIFIED | familias_out.json 'FRP' 329.74; familias_out.json 'cement board' 31.37 (D/A08.01)
ALC-21 | Shaft walls / area separation walls | NOT APPLICABLE | NOT APPLICABLE: A12.01 partition schedule has no shaft wall / area separation type; A02.01 floor plan draws no shaft (single-story bank building)
ALC-22 | Rated assemblies (UL designs) and their board type | NOT APPLICABLE | NOT APPLICABLE: A12.02 only has the finish note 'DO NOT PAINT OVER FIRE RATED STAMP'; E04.02 UL systems are typical firestop penetration details; A11.03 'FIRE RATED 3/4" PLYWOOD BACKBOARD' is a backboard (FRT plywood row); the A12.01 partition schedule lists no rated type / UL design
ALC-23 | Special panels (ballistic, lead-lined, abuse) | QUANTIFIED | familias_out.json 'ballistic panel' 83.13 (4/A12.01)
ALC-24 | Finish level (Level 4 / Level 5) | QUANTIFIED | familias_out.json 'Level 5 finish' 859.26 (A05.01 key note 9)
CLR-01 | Insulation (batt / sound attenuation / polyiso by others except the nailbase panel) | NOT APPLICABLE | EXCLUDED: insulation is excluded in all projects (estimator standing order)
CLR-02 | Storefront / office front frames DFC-1A and glazing (Div 08) | NOT APPLICABLE | EXCLUDED: storefront and office front systems by the Div 08 vendor; the framing at piers, heads, cripples and bulkheads is included
CLR-03 | Acoustical ceilings ACT (Div 09 51 00) | NOT APPLICABLE | EXCLUDED: ACT grid and tile by others; GWB ceilings, soffits and transitions are included
CLR-04 | Cement plaster / stucco PT-4, composite metal panel cladding and their accessories (J-bead, reveals) | NOT APPLICABLE | EXCLUDED: other trade; the FRT plywood substrate / sheathing and the CFMF behind them are included
CLR-05 | Light fixtures, diffusers and MEP devices (Div 23 / 26) | NOT APPLICABLE | EXCLUDED: fixtures by others; framed openings for them are included
CLR-06 | Millwork, cabinets, toilet accessories and wall-mounted equipment | NOT APPLICABLE | EXCLUDED: by others; blocking for them is included
CLR-07 | Structural steel, HSS posts and deck (Div 05 12 / 05 31) | NOT APPLICABLE | EXCLUDED: by the steel contractor; CFMF parapet infill per 11/S5.10 is included
CLR-08 | Finish level | QUANTIFIED | CLARIFICATION: Level 4 finish everywhere (joint compound yield in Inputs); Level 5 only at the wallcovering faces WC-18 / WC-20 / WC-22 that the A05.01 finish plan key notes call (Level 5 finish row); control joints not drawn, none carried
CLR-09 | Building code analysis (A00.00 project information) | QUANTIFIED | CLARIFICATION: 2021 IBC with local amendments; occupancy Group B (business); construction Type II-B; single story, 20'-0" building height; building 4,260 SF + drive-through 850 SF = 5,110 SF gross; ground-up new financial center, steel frame, slab on grade (A00.00).
CLR-10 | All work is new construction | QUANTIFIED | CLARIFICATION: ground-up building, no existing partitions to remain; no patch and repair allowance
CLR-11 | Trade criteria carried in the price | QUANTIFIED | CLARIFICATION: stud blocking at the horizontal board joint of faces taller than the sheet length; metal 362CR stud blocking where general note C gives no material; wall stop blocking one stud bay; jamb return width = stud depth; deflection (slip) track per the partition details, deflection clips not carried (RFI); power-driven pins at the closest printed spacing; waste 15% metal / 6% non-metal applied once
CLR-12 | Gypsum board on opposite faces | QUANTIFIED | CLARIFICATION: board is carried face by face (side A / side B) with its own height and layers per the partition detail; see Partition Takeoff
ALC-X37 | batt insulation | NOT APPLICABLE | EXCLUDED (estimator criterion: no insulation)

## _reglas (hidden)
reglas.py compuerta OK
{"canon": "a2d52c20d1067b866ec45b2de72351163de7db09895826d512d49777b2286c75", "evidencias": "6e29fe65d1c4457bb4c2d532bee5fef132ddeacb112b52347f4ddff71faf13c9", "familias_out": "9ab0804766f63b8650a2f627be5df5c486bb0fa2bd863ba480cfb130a51d3e1c", "reglas": "267acd5189f2c8edd3c442d4188cc010f12edb50daaf890c1d7cadf926793146", "version": "v73"}